## Sheet1
TRANSFORMER TURN RATIO REPORT
Equipment Name |  |  | 14100-TR-003 |  |  |  | Site |  | CUP-1
Serial No. |  |  | PP0084B01 |  |  |  | Power Rating |  | 40000 |  | kVA
Manufacture |  |  | DAIHEN |  |  |  | Voltage Rating |  | 115 /22 |  | / kV
Fluid Type |  |  | Mineral Oil |  |  |  | Service Type |  | Distri | bution Tr | ansformer
Test Information | [7 empty] | Enviroment
Test Instrument |  |  | TESTRANO 600 |  |  |  | Ambient Temp. |  |  | °C
Serial Number |  |  | DA193X |  |  |  |  | Oil Temp. |  | °C
Calibration Date |  |  | 46006 |  |  |  | Winding Temp. |  |  | °C
[8 empty] | Humidity. |  | %
Ratio from nameplate
1Vector Group: T2ap |  |  | Dyn1 HV 3 | No of 4 | Winding : 5 | 2 6 | 7 | 8 | 9 | 10
|  | T2ap | HV 3 Voltage | 4 LV Voltage | 5 Turn Ratio | 6 Tap | 7 HV Voltage | 8 TV Voltage | 9 Turn Ratio
|  | Position | (V) | (V) | Cal. | Position | (V) | (V) | Cal.
| Max |  | 126500 | 22000 | 9.959 | Max |  |  | -
| Center |  | 115000 | 22000 | 9.054 | Center |  |  | -
| Min |  | 103500 | 22000 | 8.148 | Min |  |  | -
| Tap: |  | - | - | - | Tap: | - | - | -
| Tap: |  | - | - | - | Tap: | - | - | -
1 |  | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10
Turn Ratio between HV-LV
Te | st | 2: Voltage; 3: 200; 4: V
|  |  | Connect: | H1-H2 : X1-X0 |  | Connect: | H2-H3 : X2-X0 |  | Connect: | H3-H1 : X3-X0
|  | Tap | Turn | %Error | Phase | Turn | %Error | Phase | Turn | %Error | Phase | Max
Position
|  | 3: Ratio; 5: %Deviation; 6: Ratio; 8: %Deviation; 9: Ratio | %Deviation | %Error
| Max |  | 9.938 | 0.21 | - | 9.938 | 0.21 | - | 9.937 | 0.22 | - | 0.22
| Center |  | 9.035 | 0.21 | - | 9.034 | 0.22 | - | 9.034 | 0.22 | - | 0.22
| Min |  | 8.131 | 0.21 | - | 8.131 | 0.21 | - | 8.13 | 0.22 | - | 0.22
| Tap: - | [9 empty] | - | - | bar: 3 to 10
| Tap: - | [9 empty] | - | - | bar: 3 to 10
Turn Rati | o | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10
Turn Ratio |  | 2 3 between HV-TV |  | 4 | 5 | 6 | 7 | 8 | 9 | 10
Test Voltage | bar: 3 to 4
|  |  | Connect: | H1-H2 : Y1-Y0 |  | Connect: | H2-H3 : Y2-Y0 |  | Connect: | H3-H1 : Y3-Y0
|  | Tap | Turn | %Error | Phase | Turn | %Error | Phase | Turn | %Error | Phase | Max
Position
|  | 3: Ratio; 5: %Deviation; 6: Ratio; 8: %Deviation; 9: Ratio | %Deviation | %Error
| Max | [9 empty] | - | - | bar: 3 to 7; 9 to 10
| Center | [9 empty] | - | - | bar: 3 to 10
| Min | [9 empty] | - | - | bar: 3 to 10
| Tap: - | [9 empty] | - | - | bar: 3 to 10
| Tap: - | [9 empty] | - | - | bar: 3 to 10
Criteria: IEEE 2 |  |  | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10
Criteria: IEEE 2 C57.152-2013 |  |  | 3 C57.152-2013 | 4 | 5 | 6 | 7 | 8 | 9 | 10
| ± 0.5% Deviate from name plate. | ± 0.5% Deviate from name plate. | 3: ± 0.5% Deviate from name plate.; 4: ± 0.5% Deviate from name plate.
Response |  |  | 3: Tested By; 6: Tested By; 10: Approved By
Company |  |  | 3: GPSC; 10: GPSC
Name |  |  | 3: Mr.Jirasak S.; 10: Mr.Suchart M.
Signature
Date |  |  | 3: 14-Jul-2026; 6: 14-Jul-2026; 10: 14-Jul-2026