## Transformer_Plan
WBS | SAP_MO | Parent_WBS | Task_Description | Lead | Transformer_Tag | Plant | Category | Start_Date | End_Date | Days | Progress | Cost
TO1 | 40001001 |  | GHECO-ONE: Outage Year 2026 | MMT | KT1A | GHECO-ONE | Transformer Outage | 2026-01-05 | 2026-01-27 | 22 | 100 | 75260
TO2 | 40001002 |  | GT42 3Y PM 2026 | PIP | GT42 GSUT | GEN Ph.2 | Transformer Outage | 2026-01-06 | 2026-01-09 | 4 | 100 | 0
TO2.1 | 40001003 | TO2 | Install Scaffolding | PIP | GT42 GSUT | GEN Ph.2 | Transformer Outage | 2026-01-06 | 2026-01-07 | 2 | 100 | 0
TO2.2 | 40001004 | TO2 | Preventive Program by EMM | PIP | GT42 GSUT | GEN Ph.2 | Transformer Outage | 2026-01-07 | 2026-01-09 | 3 | 100 | 0
TO3 | 40001005 |  | CUP-1: GTG16 3Y PM 2026 | JIS | GTG16 GSUT | CUP-1 | Transformer Outage | 2026-01-09 | 2026-01-12 | 4 | 100 | 35800
TO3.1 | 40001006 | TO3 | Install Scaffolding | JIS | GTG16 GSUT | CUP-1 | Transformer Outage | 2026-01-09 | 2026-01-10 | 2 | 100 | 15000
TO3.2 | 40001007 | TO3 | Preventive Program by EMM | JIS | GTG16 GSUT | CUP-1 | Transformer Outage | 2026-01-10 | 2026-01-12 | 3 | 100 | 20800
TO4 | 40001008 |  | GEN: GT61 3Y PM 2026 | PIP | GT61 GSUT | GEN Ph.2 | Transformer Outage | 2026-01-23 | 2026-01-27 | 5 | 100 | 0
TO5 | 40001009 |  | GEN: GT62 3Y PM 2026 | PIP | GT62 GSUT | GEN Ph.2 | Transformer Outage | 2026-02-10 | 2026-02-14 | 5 | 0 | 0
TO5.1 | 40001010 | TO5 | Install Scaffolding | PIP | GT62 GSUT | GEN Ph.2 | Transformer Outage | 2026-02-10 | 2026-02-11 | 2 | 0 | 0
TO5.2 | 40001011 | TO5 | Preventive Program by EMM | JIS | GT62 GSUT | GEN Ph.2 | Transformer Outage | 2026-02-11 | 2026-02-14 | 4 | 0 | 0
TO6 | 40001012 |  | GSPP2&3: STG3C GSUT 3Y PM 2026 | PIP | STG3C GSUT | GSPP2&3 | Transformer Outage | 2026-03-03 | 2026-03-07 | 5 | 0 | 0
TO6.1 | 40001013 | TO6 | Install Scaffolding | PIP | STG3C GSUT | GSPP2&3 | Transformer Outage | 2026-03-03 | 2026-03-04 | 2 | 0 | 0
TO6.2 | 40001014 | TO6 | Preventive Program by EMM | JIS | STG3C GSUT | GSPP2&3 | Transformer Outage | 2026-03-04 | 2026-03-07 | 4 | 0 | 0
TO7 | 40001015 |  | GEN: GT2B 3Y PM 2026 | PIP | GT2B GSUT | GEN Ph.2 | Transformer Outage | 2026-04-27 | 2026-05-01 | 5 | 40 | 0
PA1 | 40001016 |  | 11BAT10 PM&Assessment 2026 | PIP | 11BAT10 | GIPP | Plant Assessment | 2026-03-01 | 2026-03-05 | 5 | 100 | 0
LA1 | 40001017 |  | CUP-1: Transformer Life Assessment | MMT | GTG16 GSUT | CUP-1 | Life Assessment | 2026-02-15 | 2026-02-28 | 14 | 100 | 45000
OL1 | 40001018 |  | GEN Ph.2: OLTC Diagnostic & Inspection | PIP | GT42 GSUT | GEN Ph.2 | OLTC Inspection | 2026-03-10 | 2026-03-18 | 8 | 50 | 28000
VS1 | 40001019 |  | 3 Months Visual CUP-1_Q1 | JIS | All TRs | CUP-1 | 3M Visual | 2026-01-01 | 2026-01-31 | 31 | 0 | 0
VS2 | 40001020 |  | 3 Months Visual CUP-2_Q1 | JIS | All TRs | CUP-2 | 3M Visual | 2026-01-01 | 2026-01-31 | 31 | 0 | 0
VS3 | 40001021 |  | 3 Months Visual CUP-1_Q2 | JIS | All TRs | CUP-1 | 3M Visual | 2026-04-01 | 2026-04-30 | 30 | 0 | 0
VS4 | 40001022 |  | 3 Months Visual CUP-1_Q3 | JIS | All TRs | CUP-1 | 3M Visual | 2026-07-01 | 2026-07-31 | 31 | 0 | 0
VS5 | 40001023 |  | 3 Months Visual CUP-1_Q4 | JIS | All TRs | CUP-1 | 3M Visual | 2026-10-01 | 2026-10-31 | 31 | 0 | 0
OA1 | 40001024 |  | 6 Months Oil Analysis CUP-1 | JIS | Main TRs | CUP-1 | Oil Analysis | 2026-04-01 | 2026-04-30 | 30 | 0 | 0
OA2 | 40001025 |  | 12 Months Oil Analysis CUP-1 | JIS | All TRs | CUP-1 | Oil Analysis | 2026-10-01 | 2026-10-31 | 31 | 100 | 0
OA2.1 | 40001026 | OA2 | PR for Oil sampling CUP-1 | PIP | Sampling | CUP-1 | Oil Analysis | 2026-10-01 | 2026-10-31 | 31 | 100 | 0

## Health_Index_Fleet
﻿No. | Equipment Name | Serial No | SITE | Rated Power (MVA) | HV Rate (kV) | LV Rate (kV) | Rated Voltage (kV) | Service Type | Service Age (Year) | Condition Health Index | Health Index Status | Estimated DP (From Furan) | Estimated Remaining Life time (Year) | Visual Inspection | Active Part | Insulation Resistance & PI | Insulation Power Factor | Exciting Current | Ratio&Polarity | Winding Resistance | 1∅ Short Circuit Impedance | 3∅ Short Circuit Impedance | Core to Ground | Bushing | Surge Arrester | Dynamic Resistance Measurement (OLTC) | Frequency Response Analysis (FRA) | %Moisture in paper (FDS) | Main Tank Oil | DGA | Water Content | Dielectric Breakdown | PF at 25 °C | PF at 100 °C | Conductivity | Interfratial Tension (IFT) | Acidity | Color | Inhibitor | Corrosive Sulfur | Passivator | Furan | Sludge | OLTC Oil | DGA (OLTC) | Dielectric Breakdown (OLTC) | Water Content (OLTC) | Date To Assess | FAT | 2011 | 2012 | 2013 | Last PM | Next PM | Recommendation
0 | 16120-TR-001 | 4803321 | CUP-1 | 6 | 11 | 6.9 | 11/6.9 | UAT | 21 | 69 | Warning | 937 |  | Q | A | A | A | A | A | A | A | A | N/A | N/A | N/A | N/A | A | A | Q | Q | A | A | A | Q | A | A | A | A | A | Q | Q | A | A | N/A | N/A | N/A | N/A | 01/19/2026 |  |  |  |  | 2025 | 2028 | "Repair oil leak and hot oil purify, Add passivator. Plan for oil regeneration/Change Oil: Concern oil conductivity is unacceptable limit, Suspect corrosive (3b),"
0 | 16120-TR-003 | 4902687 | CUP-1 | 6 | 11 | 6.9 | 11/6.9 | UAT | 20 | 86 | Healthy | 1003 |  | A | A | A | A | A | A | A | A | A | N/A | N/A | N/A | N/A | N/A | N/A | Q | Q | A | A | A | A | A | A | A | A | A | Q | Q | A | A | N/A | N/A | N/A | N/A | 01/19/2026 |  |  |  |  | 2023 | 2026 | "Add passivator, Plan for oil regeneration/Change Oil: Concern oil conductivity is unacceptable limit, Suspect corrosive (3b)."
0 | 16120-TR-004 | 5001769 | CUP-1 | 6 | 11 | 6.9 | 11/6.9 | UAT | 19 | 83 | Healthy | 1003 |  | A | A | A | A | A | A | A | A | A | N/A | N/A | N/A | N/A | A | Q | Q | Q | A | A | A | A | A | A | A | A | A | Q | Q | A | A | N/A | N/A | N/A | N/A | 01/19/2026 |  |  |  |  | 2021 | 2024 | "Plan for oil regeneration/Change Oil: Concern IFT is unacceptable limit and conductivity is questionable limit, Suspect corrosive (3b), Add passivator. Plan for drying transformer (insulation paper degradation)."
0 | 16120-TR-006 | 5101711 | CUP-1 | 6 | 11 | 6.9 | 11/6.9 | UAT | 21 | 83 | Healthy | 1003 |  | A | A | A | A | A | A | Q | A | A | N/A | N/A | N/A | N/A | A | Q | Q | Q | A | A | A | A | A | A | A | A | A | Q | A | A | A | N/A | N/A | N/A | N/A | 01/19/2026 |  |  |  |  | 2025 | 2028 | Plan for oil regeneration/Change Oil: Concern conductivity is unacceptable limit and IFT is questionable limit. Plan for drying transformer (insulation paper degradation).
0 | 10060-TR-101 | 5201090 | CUP-1 | 6 | 11 | 6.9 | 11/6.9 | UAT | 17 | 60 | Warning | 1031 |  | Q | Q | A | U | Q | A | A | A | A | N/A | N/A | N/A | N/A | N/A | N/A | A | A | Q | A | A | Q | A | A | A | A | N/A | A | A | A | A | N/A | N/A | N/A | N/A | 01/20/2026 |  |  |  |  | 2025 | 2028 | Follow power factor test period shutdown and DFR test.
0 | 10060-TR-102 | 5201091 | CUP-1 | 6 | 11 | 6.9 | 11/6.9 | UAT | 17 | 60 | Warning | 1152 |  | Q | A | A | A | U | A | A | A | A | N/A | N/A | N/A | N/A | N/A | N/A | A | A | Q | A | A | Q | A | A | A | A | N/A | Q | A | A | Q | N/A | N/A | N/A | N/A | 01/20/2026 |  |  |  |  | 2023 | 2026
0 | 14100-TR-001 (GTG11) | 4810106 | CUP-1 | 55 | 115 | 10.5 | 115/10.5 | GSUT | 21 | 86 | Healthy | 970 |  | A | A | A | A | A | A | A | A | A | N/A | A | U | N/A | A | A | Q | A | A | A | A | A | A | A | A | A | A | A | A | A | N/A | N/A | N/A | N/A | N/A | 01/19/2026 |  |  |  |  | 2025 | 2028 | Plan for oil regeneration: Concern oil conductivity and IFT are questionable limit.
0 | 14100-TR-002 (GTG12) | 4811735 | CUP-1 | 55 | 115 | 10.5 | 115/10.5 | GSUT | 20 | 89 | Healthy | 859 |  | A | A | A | A | A | A | A | A | A | N/A | A | A | N/A | A | A | Q | Q | A | A | A | A | A | A | A | A | A | A | A | A | A | N/A | N/A | N/A | N/A | 01/19/2026 |  |  |  |  | 2023 | 2026 | "Repair hot spot: HV cable terminator phase A and B (Max. 52 °C), Plan for oil regeneration: Concern IFT are questionable limit, Add passivator."
0 | 14100-TR-005 (GTG13) | PP0174B01 | CUP-1 | 55 | 115 | 10.5 | 115/10.5 | GSUT | 18 | 89 | Healthy | 862 |  | A | A | A | A | A | A | A | A | A | N/A | A | A | N/A | A | A | Q | A | A | A | A | A | A | A | A | A | A | Q | A | A | A | N/A | N/A | N/A | N/A | 01/19/2026 |  |  |  |  | 2024 | 2027 | Plan for oil regeneration: Concern oil conductivity is unacceptable limit.
0 | 14100-TR-006 (GTG14) | PP0225B01 | CUP-1 | 55 | 115 | 10.5 | 115/10.5 | GSUT | 17 | 90 | Healthy | 961 |  | A | A | A | A | A | A | A | A | A | N/A | A | A | N/A | A | A | Q | A | A | A | A | A | A | A | A | A | A | A | Q | A | A | N/A | N/A | N/A | N/A | 01/19/2026 |  |  |  |  | 2025 | 2028 | Plan for oil regeneration: Concern IFT is unacceptable limit and conductivity is questionable limit.
0 | 10060-TR-001 (GTG15) | 5110021 | CUP-1 | 55 | 118 | 11 | 118/11 | GSUT | 18 | 94 | Healthy | 945 |  | A | A | A | A | A | A | A | A | A | N/A | A | A | N/A | A | A | Q | A | A | A | A | A | A | A | A | A | A | A | A | A | A | N/A | N/A | N/A | N/A | 01/19/2026 |  |  |  |  | 2025 | 2028 | Plan for oil regeneration: Concern IFT is unacceptable limit.
0 | 10060-TR-002 (GTG16) | 5110022 | CUP-1 | 55 | 118 | 11 | 118/11 | GSUT | 18 | 91 | Healthy | 806 |  | A | A | A | A | A | A | A | A | A | N/A | A | A | N/A | A | A | Q | Q | A | A | A | A | A | A | A | A | A | A | A | A | A | N/A | N/A | N/A | N/A | 01/19/2026 |  |  |  |  | 2026 | 2029 | Plan for oil regeneration: Concern IFT is unacceptable limit.
0 | 14100-TR-003 | PP0084B01 | CUP-1 | 40 | 115 | 22 | 115/22 | Distribution | 20 | 83 | Healthy | 1053 |  | A | A | A | A | A | A | A | A | A | N/A | A | Q | A | A | A | Q | A | A | A | A | Q | A | A | A | A | A | Q | Q | A | A | A | A | A | A | 01/19/2026 |  |  |  |  | 2023 | 2026 | "Plan for oil regeneration: Concern oil conductivity is unacceptable limit, Suspect corrosive (3b), Add passivator."
0 | 14100-TR-004 | PP0102B01 | CUP-1 | 40 | 115 | 22 | 115/22 | Distribution | 20 | 88 | Healthy | 931 |  | A | A | A | A | A | A | A | A | A | N/A | A | A | A | A | A | A | Q | A | A | A | A | A | A | A | A | A | A | A | A | A | A | A | A | A | 01/19/2026 |  |  |  |  | 2023 | 2026 | Routine 3Y PM Program.
0 | 16120-TR-002A | 4803168 | CUP-1 | 2.66 | 6.9 | 0.4 | 6.9/0.4 | Auxiliary | 21 | 66 | Warning | - |  | Q | Q | Q | A | A | A | Q | A | A | N/A | N/A | N/A | N/A | A | A | A | Q | A | A | A | A | A | A | A | A | A | A | A | A | A | N/A | N/A | N/A | N/A | 01/19/2026 |  |  |  |  | 2025 | 2028 | "Plan for oil top-up and N2 fill up for Positive Pressure, Follow to confirm test: Insulation resistance."
0 | 16120-TR-002B | 4803167 | CUP-1 | 2.66 | 6.9 | 0.4 | 6.9/0.4 | Auxiliary | 21 | 74 | Monitor | - |  | A | Q | A | A | A | A | A | Q | A | N/A | N/A | N/A | N/A | N/A | N/A | Q | Q | Q | A | A | A | A | A | A | A | N/A | Q | Q | A | A | N/A | N/A | N/A | N/A | 01/20/2026 |  |  |  |  | 2023 | 2026 | "Plan for oil top-up and N2 fill up for Positive Pressure, Plan for oil regeneration: Concern oil conductivity is questionable limit, Re-test Insulation resistance and short circuit test."
0 | 16120-TR-005A | 5001766 | CUP-1 | 1.6 | 6.9 | 0.4 | 6.9/0.4 | Auxiliary | 19 | 86 | Healthy | 1066 |  | A | A | A | A | A | A | Q | A | A | N/A | N/A | N/A | N/A | N/A | N/A | Q | Q | A | A | A | A | A | A | A | A | N/A | A | A | A | A | N/A | N/A | N/A | N/A | 01/20/2026 |  |  |  |  | 2021 | 2024 | "Plan for oil regeneration: Concern IFT is unacceptable limit and conductivity is questionable limit., Re-test 1 and 3 Phase Short Circuit."
0 | 16120-TR-005B | 5001700 | CUP-1 | 1.6 | 6.9 | 0.4 | 6.9/0.4 | Auxiliary | 19 | 49 | Critical | 930 |  | A | A | A | A | A | A | A | A | A | N/A | N/A | N/A | N/A | A | N/A | Q | Q | A | U | A | A | A | A | A | A | N/A | Q | A | A | A | N/A | N/A | N/A | N/A | 03/01/2026 |  |  |  |  | 2025 | 2028 | Replacement new oil and hot oil purify in the next shutdown.
0 | 10060-TR-201 | 5200523 | CUP-1 | 1.6 | 6.9 | 0.4 | 6.9/0.4 | Auxiliary | 17 | 77 | Monitor | 1047 |  | A | Q | Q | U | U | A | A | A | A | N/A | N/A | N/A | N/A | A | N/A | A | A | Q | A | A | Q | A | A | A | A | N/A | Q | A | A | Q | N/A | N/A | N/A | N/A | 03/01/2026 |  |  |  |  | 2025 | 2028 | "Plan for oil top up, Re-test the Insulaion resistance and power factor (If not pass, require to change new oil.)"
0 | 10060-TR-202 | 5200524 | CUP-1 | 1.6 | 6.9 | 0.4 | 6.9/0.4 | Auxiliary | 17 | 77 | Monitor | 930 |  | A | Q | A | A | A | A | A | Q | Q | N/A | N/A | N/A | N/A | N/A | N/A | A | Q | Q | A | A | Q | A | A | Q | A | N/A | Q | A | A | Q | N/A | N/A | N/A | N/A | 03/01/2026 |  |  |  |  | 2022 | 2025 | "Plan for oil top up, Re-test 1 and 3 Phase short circuit impedance."
0 | 24201-TR-011 | 4912022 | CUP-2 | 8.8 | 11 | 7 | 11/7 | UAT | 19 | 93 | Healthy | 1066 |  | A | A | A | A | A | A | A | A | A | A | N/A | N/A | A | A | N/A | Q | A | A | A | A | Q | A | A | A | A | N/A | A | A | A | A | A | A | A | A | 03/01/2026 |  |  |  |  | 2023 | 2026 | "Hot oil purify, Concern PF 100 °C, Condutivity are unacceaptable limit, IFT is questionable limit."
0 | 24201-TR-012 | 4912023 | CUP-2 | 8.8 | 11 | 7 | 11/7 | UAT | 19 | 93 | Healthy | 1089 |  | A | A | A | A | A | A | A | A | A | A | N/A | N/A | A | A | N/A | Q | A | A | A | A | Q | A | A | A | A | N/A | A | A | A | A | A | A | A | A | 03/01/2026 |  |  |  |  | 2023 | 2026 | "Hot oil purify, Concern PF 100 °C, Condutivity are unacceaptable limit, IFT is questionable limit."
0 | 23901-TR-011 (GTG21) | 4912019 | CUP-2 | 55 | 117 | 11 | 117/11 | GSUT | 19 | 69 | Warning | 900 |  | Q | A | A | A | A | A | A | A | A | A | A | A | N/A | A | A | Q | Q | A | A | A | A | A | A | A | A | N/A | A | Q | A | A | N/A | N/A | N/A | N/A | 03/01/2026 |  |  |  |  | 2024 | 2027 | "Plan for oil regeneration, Concern IFT, Condutivity are unacceaptable limit, Color is questionable limit."
0 | 23902-TR-012 (GTG22) | 4912020 | CUP-2 | 55 | 117 | 11 | 117/11 | GSUT | 19 | 74 | Monitor | 980 |  | Q | A | A | A | A | A | A | A | A | A | A | A | N/A | A | A | Q | A | A | A | A | A | A | A | A | A | N/A | A | A | A | A | N/A | N/A | N/A | N/A | 03/01/2026 |  |  |  |  | 2024 | 2027 | Plan for oil regeneration; there is a concern that the IFT is below the acceptable limit.
0 | 23911-TR-010 (STG21) | 4912021 | CUP-2 | 54 | 117 | 11 | 117/11 | GSUT | 19 | 83 | Healthy | 884 |  | A | A | A | A | A | A | A | A | A | A | A | A | N/A | A | A | Q | Q | A | A | A | A | A | A | A | A | N/A | A | A | A | A | N/A | N/A | N/A | N/A | 03/01/2026 |  |  |  |  | 2023 | 2026 | Plan for oil regeneration; there is a concern that the IFT is decrease closely the acceptable limit.
0 | 24201-TR-111 | 5000574 | CUP-2 | 2 | 6.9 | 0.4 | 6.9/0.4 | Auxiliary | 19 | 80 | Healthy | 1003 |  | A | Q | A | A | A | A | Q | U | A | N/A | N/A | N/A | N/A | A | N/A | Q | Q | A | A | A | A | A | A | A | A | N/A | A | A | A | A | N/A | N/A | N/A | N/A | 03/01/2026 |  |  |  |  | 2025 | 2028 | Plan for oil regeneration; there is a concern that the IFT Conductivity are qeustionable limit. Re-test Insulation resistance and short circuit test.
0 | 24201-TR-112 | 5000575 | CUP-2 | 2 | 6.9 | 0.4 | 6.9/0.4 | Auxiliary | 19 | 94 | Healthy | 1066 |  | A | Q | A | A | A | A | Q | Q | A | N/A | N/A | N/A | N/A | A | N/A | Q | A | A | A | A | A | A | A | A | A | N/A | A | A | A | A | N/A | N/A | N/A | N/A | 03/01/2026 |  |  |  |  | 2025 | 2028 | Plan for oil regeneration; there is a concern that the Conductivity and Color are qeustionable limit. Re-test short circuit test.
0 | 24201-TR-121 | 5000576 | CUP-2 | 2 | 6.9 | 0.4 | 6.9/0.4 | Auxiliary | 19 | 89 | Healthy | 1047 |  | A | Q | A | A | A | A | Q | A | A | N/A | N/A | N/A | N/A | A | N/A | Q | Q | A | A | A | A | A | A | A | A | N/A | A | A | A | A | N/A | N/A | N/A | N/A | 03/01/2026 |  |  |  |  | 2025 | 2028 | Plan for oil regeneration; there is a concern that the Conductivity and Color are qeustionable limit. Re-test short circuit test.
0 | 24201-TR-122 | 5000577 | CUP-2 | 2 | 6.9 | 0.4 | 6.9/0.4 | Auxiliary | 19 | 89 | Healthy | 1066 |  | A | Q | A | A | A | A | Q | Q | Q | N/A | N/A | N/A | N/A | A | N/A | Q | Q | A | A | A | A | A | A | A | A | N/A | A | A | A | A | N/A | N/A | N/A | N/A | 03/01/2026 |  |  |  |  | 2025 | 2028 | Plan for oil regeneration; there is a concern that the Conductivity is qeustionable limit. Re-test short circuit test.
0 | 36120-TR-103 (STG31) | 5110023 | CUP-3 | 21 | 118 | 11 | 118/11 | GSUT | 18 | 83 | Healthy | 1152 |  | A | A | A | A | A | A | A | A | A | N/A | A | A | N/A | A | A | A | Q | A | A | A | A | A | A | A | A | A | Q | A | A | A | N/A | N/A | N/A | N/A | 03/01/2026 |  |  |  |  | 2025 | 2028 | Routine 3Y PM Program.
0 | 34101-TR-001 | PP0158B01 | CUP-3 | 40 | 115 | 22 | 115/22 | Distribution | 18 | 85 | Healthy | 1089 |  | A | A | A | A | A | A | A | A | A | N/A | A | A | A | A | A | A | Q | A | A | A | A | A | A | A | A | A | A | A | A | A | A | A | A | A | 03/01/2026 |  |  |  |  | 2023 | 2026 | Routine 3Y PM Program.
0 | 34101-TR-002 | PP0181B01 | CUP-3 | 40 | 115 | 22 | 115/22 | Distribution | 18 | 88 | Healthy | 1089 |  | A | A | A | A | A | A | A | A | A | N/A | A | A | A | A | A | A | Q | A | A | A | A | A | A | A | A | A | A | A | A | A | A | A | A | A | 03/01/2026 |  |  |  |  | 2023 | 2026 | Routine 3Y PM Program.
0 | 36120-TR-201 | 5102852 | CUP-3 | 10 | 22 | 6.9 | 22/6.9 | Auxiliary | 18 | 91 | Healthy | 1031 |  | A | A | A | A | A | A | A | A | A | N/A | N/A | N/A | N/A | N/A | N/A | Q | Q | A | A | A | A | A | A | A | A | N/A | A | A | A | A | N/A | N/A | N/A | N/A | 03/01/2026 |  |  |  |  | 2022 | 2025 | "3Y PM program overdue, Plan for oil reganeration; there is a concern that the Conductivity is qeustionable limit."
0 | 36120-TR-202 | 5103176 | CUP-3 | 10 | 22 | 6.9 | 22/6.9 | Auxiliary | 18 | 74 | Monitor | 1089 |  | Q | A | A | A | A | A | A | A | A | N/A | N/A | N/A | N/A | N/A | Q | A | Q | A | A | A | A | A | A | A | A | N/A | A | A | A | A | N/A | N/A | N/A | N/A | 03/01/2026 |  |  |  |  | 2022 | 2025 | 3Y PM program overdue. Re-test 1 phase short circuit.
0 | 36120-TR-301 | 5103168 | CUP-3 | 2 | 6.6 | 0.4 | 6.6/0.4 | Auxiliary | 18 | 86 | Healthy | 1117 |  | A | A | A | A | A | A | Q | Q | A | N/A | N/A | N/A | N/A | A | N/A | A | Q | A | A | A | A | A | A | A | A | N/A | A | A | A | A | N/A | N/A | N/A | N/A | 03/01/2026 |  |  |  |  | 2022 | 2025 | "3Y PM program overdue, Re-test 1 phase short circuit."
0 | 36120-TR-302 | 5103169 | CUP-3 | 2 | 6.6 | 0.4 | 6.6/0.4 | Auxiliary | 18 | 83 | Healthy | 1089 |  | A | Q | A | A | A | A | Q | Q | A | N/A | N/A | N/A | N/A | A | N/A | Q | Q | A | A | A | Q | A | A | A | A | N/A | A | A | A | A | N/A | N/A | N/A | N/A | 03/01/2026 |  |  |  |  | 2022 | 2025 | "3Y PM program overdue, Re-test 1 phase short circuit, Plan for oil regeneration (PF 100C, Conductivity, IFT)."
0 | 36120-TR-303 | 5103170 | CUP-3 | 2 | 6.6 | 0.4 | 6.6/0.4 | Auxiliary | 18 | 86 | Healthy | 1016 |  | A | Q | A | U | A | A | Q | U | A | N/A | N/A | N/A | N/A | A | N/A | Q | A | A | A | A | A | A | A | A | A | N/A | A | A | A | A | N/A | N/A | N/A | N/A | 03/01/2026 |  |  |  |  | 2022 | 2025 | "3Y PM program overdue, Re-test short circuit, Power factor, Plan for oil regeneration (Conductivity, Sludge)."
0 | 36120-TR-304 | 5103171 | CUP-3 | 2 | 6.6 | 0.4 | 6.6/0.4 | Auxiliary | 18 | 89 | Healthy | 1152 |  | A | A | A | Q | A | A | A | Q | A | N/A | N/A | N/A | N/A | A | N/A | Q | A | A | A | A | A | A | A | A | A | N/A | Q | A | A | A | N/A | N/A | N/A | N/A | 03/01/2026 |  |  |  |  | 2022 | 2025 | "3Y PM program overdue, Re-test short circuit, Power factor, Plan for hot oil purify (Sludge)."
0 | 41BAT01 (GTG41) | 6110201 | CUP-4 | 91 | 115 | 11 | 115/11 | GSUT | 8 | 90 | Healthy | 1066 | [35 empty] | 03/01/2026 |  |  |  |  | 2023 | 2026 | Routine 6Y PM Program (Overhaul OLTC). | bar: A to N/A
0 | 41BAT02 | 6110202 | CUP-4 | 52 | 115 | 22 | 115/22 | Distribution | 7 | 88 | Healthy | 1066 | [35 empty] | 03/01/2026 |  |  |  |  | 2024 | 2027 | Routine 6Y PM Program (Overhaul OLTC). | bar: A to N/A
0 | 41BBT20GT001 | 6110203 | CUP-4 | 10 | 11 | 6.9 | 11/6.9 | UAT | 7 | 80 | Healthy | 1031 |  | A | A | A | A | A | A | A | A | A | N/A | N/A | N/A | A | N/A | N/A | Q | Q | A | A | A | A | A | A | A | A | A | Q | A | A | A | A | A | A | A | 04/01/2026 |  |  |  |  | 2023 | 2026 | Plan for oil regeneration: Concern oil conductivity is unacceptable limit.
0 | 41BFT20GT001 | 6110204 | CUP-4 | 2.8 | 6.6 | 0.4 | 6.6/0.4 | Auxiliary | 7 | 86 | Healthy | 1200 |  | A | Q | A | A | N/A | A | A | A | A | N/A | N/A | N/A | N/A | N/A | N/A | Q | A | A | A | A | A | A | A | A | A | A | A | A | A | A | A | A | A | A | 04/01/2026 |  |  |  |  | 2023 | 2026 | Plan for oil regeneration: Concern oil conductivity and IFT are questionable limit.
0 | 41BFT80GT001 | 6110245 | CUP-4 | 1 | 6.6 | 0.4 | 6.6/0.4 | Auxiliary | 7 | 90 | Healthy | 1117 | 25 | A | A | A | A | A | A | A |  |  |  | A | A |  |  |  | Q | A | A | A | A | A | A | A | Q | A | N/A | Q | A | A | A | N/A | N/A | N/A | N/A | 04/01/2026 |  |  |  |  | 2024 | 2027 | Update PM data. Plan for oil regeneration: Concern oil conductivity is unacceptable limit.
1 | 41BBT10 | 6410137 | GEN | 6 | 11 | 6.6 | 11/6.6 | UAT | 5 | 89 | Healthy | 1152 |  | A | A | A | A | A | A | A | N/A | N/A | A | N/A | N/A | N/A | N/A | N/A | A | Q | A | A | A | A | A | A | A | A | N/A | Q | A | A | A | N/A | N/A | N/A | N/A | 04/01/2026 |  |  |  |  | 2021 | 2024 | 3Y PM Program overdue.
2 | 42BBT10 | 6410130 | GEN | 6 | 11 | 6.6 | 11/6.6 | UAT | 5 | 89 | Healthy | 1152 |  | A | A | A | A | A | A | A | N/A | N/A | A | N/A | N/A | N/A | N/A | N/A | A | Q | A | A | A | A | A | A | A | A | N/A | Q | A | A | A | N/A | N/A | N/A | N/A | 04/01/2026 |  |  |  |  | 2021 | 2024 | 3Y PM Program overdue.
3 | 61BBT10 | 6410131 | GEN | 6 | 11 | 6.6 | 11/6.6 | UAT | 5 | 89 | Healthy | 1152 |  | A | A | A | A | A | A | A | N/A | N/A | A | N/A | N/A | N/A | N/A | N/A | A | Q | A | A | A | A | A | A | A | A | N/A | Q | A | A | A | N/A | N/A | N/A | N/A | 04/01/2026 |  |  |  |  | 2021 | 2024 | 3Y PM Program overdue.
4 | 62BBT10 | 6410132 | GEN | 6 | 11 | 6.6 | 11/6.6 | UAT | 5 | 80 | Healthy | 1152 | 25 | A | A | A | A | A | A | A | N/A | N/A | A | A | A |  |  |  | A | Q | A | A | A | A | A | A | A | A |  | Q | A | A | A | [9 empty] | 2025 | - | Routine Inspection & Maintenance.
5 | GT2B GSUT | 4710348 | GEN | 50 | 123 | 11 | 123/11 | GSUT | 21 | 88 | Healthy | 905 |  | A | A | A | A | A | A | A | A | A | N/A | A | Q | N/A | A | A | Q | A | A | A | A | A | A | A | A | A | A | A | Q | A | A | N/A | N/A | N/A | N/A | 04/01/2026 |  |  |  |  | 2024 | 2027 | "Replacement buchholz relay (oil leak), Add passivator and budget plan for oil regeneration (IFT questinable limit)."
6 | GT2C GSUT | 4710349 | GEN | 50 | 123 | 11 | 123/11 | GSUT | 21 | 83 | Healthy | 930 |  | A | A | A | A | A | A | A | A | A | N/A | A | U | N/A | N/A | N/A | A | A | A | A | A | A | A | A | A | A | A | A | A | A | A | N/A | N/A | N/A | N/A | 04/01/2026 |  |  |  |  | 2023 | 2026 | Add passivator and budget plan for oil regeneration (IFT questinable limit).
7 | 41BAT10 (GTG41) | 6310537 | GEN | 65 | 120 | 11 | 120/11 | GSUT | 5 | 78 | Monitor | 1066 | 25 | [39 empty] | 2025 | - | Routine Inspection & Maintenance. | bar: A to A; N/A to N/A; Q to A; A to A
8 | 42BAT10 (GTG42) | 6310535 | GEN | 65 | 120 | 11 | 120/11 | GSUT | 5 | 85 | Healthy | 1117 | 25 | [39 empty] | 2026 | - | Routine Inspection & Maintenance. | bar: A to A; N/A to N/A; Q to A; A to A
9 | 61BAT10 (GTG61) | 6310534 | GEN | 65 | 120 | 11 | 120/11 | GSUT | 5 | 90 | Healthy | 1117 | 25 | [39 empty] | 2026 | - | Routine Inspection & Maintenance. | bar: A to A; N/A to N/A; Q to A; A to A
10 | 62BAT10 (GTG62) | 6310536 | GEN | 65 | 120 | 11 | 120/11 | GSUT | 5 | 90 | Healthy | 1117 | 25 | [39 empty] | 2025 | - | Routine Inspection & Maintenance. | bar: A to Q; N/A to N/A; Q to A; A to A
11 | TR1 | 54002 | GEN | 50 | 115 | 23 | 115/23 | Distribution | 32 | 88 | Healthy | 991 | 25 | [39 empty] | 2021 | - | Routine Inspection & Maintenance. | bar: A to A; N/A to N/A; Q to A; A to A
12 | TR2 | 508038 | GEN | 50 | 115 | 23 | 115/23 | Distribution | 32 | 70 | Monitor | 1047 | 25 | A | A | A | U | A | A | A | A | A |  | A | U |  |  |  | A | Q | A | A | A | A | A | A | A | A |  | Q | A | A | A | [9 empty] | 2023 | - | Routine Inspection & Maintenance.
13 | TR3 | 54001 | GEN | 50 | 115 | 23 | 115/23 | Distribution | 32 | 83 | Healthy | 1117 | 25 | A | A | A | U | A | A | A | A | A |  | A | A |  |  |  | A | Q | A | A | A | A | A | A | A | A |  | A | A | A | A | [9 empty] | 2023 | - | Routine Inspection & Maintenance.
14 | GT2B Bleeding | 383204884 | GEN | 4.5 | 11 | 6.9 | 11/6.9 | Auxiliary | 31 | 93 | Healthy | 1047 |  | A | A | A | A | A | A | A | A | A | N/A | N/A | N/A | N/A | N/A | N/A | Q | A | A | A | A | Q | A | A | A | A | N/A | A | A | A | A | N/A | N/A | N/A | N/A | 04/01/2026 |  |  |  |  | 2024 | 2027 | "Plan for oil regeneration: Concern oil conductivity is unacceptable limit, PF 100C and IFT are questionable limit."
15 | GT2C Bleeding | 383204886 | GEN | 4.5 | 11 | 6.9 | 11/6.9 | Auxiliary | 31 | 90 | Healthy | 1117 |  | A | A | A | A | Q | A | A | A | A | N/A | N/A | N/A | N/A | N/A | N/A | Q | A | A | A | A | A | A | A | A | A | N/A | Q | Q | A | A | N/A | N/A | N/A | N/A | 04/01/2026 |  |  |  |  | 2021 | 2024 | "3Y PM program overdue, Plan for oil regeneration: Concern oil conductivity is unacceptable limit, Corrosive sulfur is suspect corrosive (3b)."
16 | ETR1 | 6611059 | GEN | 315 | 22 | 0.4 | 22/0.4 | Auxiliary | 3 | 94 | Healthy | 1152 | 25 | [39 empty] | 2025 | - | Routine Inspection & Maintenance. | bar: A to Q; N/A to N/A; Q to A; A to A
17 | ETR2 | 6611060 | GEN | 315 | 22 | 0.4 | 22/0.4 | Auxiliary | 3 | 77 | Monitor | 1152 | 25 | [39 empty] | 2025 | - | Routine Inspection & Maintenance. | bar: A to Q; N/A to N/A; Q to A; A to A
18 | ETR3 | 5310991 | GEN | 315 | 22 | 0.4 | 22/0.4 | Auxiliary | 16 | 86 | Healthy | 950 | 25 | [39 empty] | 2023 | - | Routine Inspection & Maintenance. | bar: A to A; N/A to N/A; Q to A; A to A
19 | EDTRF-TCC1 (TR7) | 3905095 | GEN | 4 | 22 | 6.6 | 22/6.6 | Auxiliary | 30 | 88 | Healthy | 668 | 25 | [39 empty] | 2017 | - | Routine Inspection & Maintenance. | bar: A to A; N/A to N/A; Q to A; A to A
20 | EDTRF-TCC2 (TR6) | 56118448EE | GEN | 2 | 22 | 0.4 | 22/0.4 | Auxiliary | 13 | 95 | Healthy | 1152 | 25 | [39 empty] | 2025 | - | Routine Inspection & Maintenance. | bar: A to Q; N/A to N/A; Q to A; A to A
21 | EDTRF-TCC3 (TR5) | 50310092 | GEN | 1.6 | 22 | 0.4 | 22/0.4 | Auxiliary | 19 | 98 | Healthy | 1066 | 25 | [39 empty] | 2019 | - | Routine Inspection & Maintenance. | bar: A to A; N/A to N/A; Q to A; A to A
22 | 41BFT30 (Starting TR) | E541351_1 | GEN | 1.25 | 11 | 0.69 | 11/0.69 | Auxiliary | 5 | 100 | Healthy | 950 | 25 | [39 empty] | 2025 | - | Routine Inspection & Maintenance. | bar: A to Q; N/A to N/A; Q to A
23 | 42BFT30 (Starting TR) | E541351_2 | GEN | 1.25 | 11 | 0.69 | 11/0.69 | Auxiliary | 5 | 100 | Healthy | 950 | 25 | [39 empty] | 2025 | - | Routine Inspection & Maintenance. | bar: A to Q; N/A to N/A; Q to A
24 | 61BFT30 (Starting TR) | E541361_1 | GEN | 1.25 | 11 | 0.69 | 11/0.69 | Auxiliary | 5 | 100 | Healthy | 950 | 25 | [39 empty] | 2025 | - | Routine Inspection & Maintenance. | bar: A to Q; N/A to N/A; Q to A
25 | 62BFT30 (Starting TR) | E541361_2 | GEN | 1.25 | 11 | 0.69 | 11/0.69 | Auxiliary | 5 | 100 | Healthy | 950 | 25 | [39 empty] | 2025 | - | Routine Inspection & Maintenance. | bar: A to Q; N/A to N/A; Q to A
26 | 40BFT10 | 6410133 | GEN | 1.25 | 11 | 0.4 | 11/0.4 | Auxiliary | 5 | 100 | Healthy | 950 | 25 | [39 empty] | 2025 | - | Routine Inspection & Maintenance. | bar: A to Q; N/A to N/A; Q to A
27 | 40BFT20 | 6410134 | GEN | 1.25 | 11 | 0.4 | 11/0.4 | Auxiliary | 5 | 80 | Healthy | 1152 | 25 | [39 empty] | 2025 | - | Routine Inspection & Maintenance. | bar: A to Q; N/A to N/A; Q to A; A to A
28 | 60BFT10 | 6410135 | GEN | 1.25 | 11 | 0.4 | 11/0.4 | Auxiliary | 5 | 80 | Healthy | 1152 | 25 | [39 empty] | 2025 | - | Routine Inspection & Maintenance. | bar: A to Q; N/A to N/A; Q to A; A to A
29 | 60BFT20 | 6410136 | GEN | 1.25 | 11 | 0.4 | 11/0.4 | Auxiliary | 5 | 80 | Healthy | 1152 | 25 | [39 empty] | 2025 | - | Routine Inspection & Maintenance. | bar: A to Q; N/A to N/A; Q to A; A to A
30 | 2BBFT20 | 3902641 | GEN | 2.5 | 6.6 | 0.4 | 6.6/0.4 | Auxiliary | 30 | 88 | Healthy | 950 | 25 | A: A; Q: A; A: A; U: A; A: U; A: A; Q: Q; N/A: A; N/A: A; Q: A; A: A; A: A; A: A | [5 empty] | 2015 | - | Routine Inspection & Maintenance.
31 | 2CBFT20 | 3902642 | GEN | 2.5 | 6.6 | 0.4 | 6.6/0.4 | Auxiliary | 30 | 92 | Healthy | 950 | 25 | [39 empty] | 2015 | - | Routine Inspection & Maintenance. | bar: A to Q; N/A to N/A; Q to A
32 | 21-90-ED-XT-TR1 | 14231662_2 | GEN | 1.6 | 6.6 | 0.4 | 6.6/0.4 | Auxiliary | 33 | 80 | Healthy | - | - | A | A | A | A | U | A | A | A | A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 04/01/2026 |  |  |  |  | 2019 | 2022 | 3Y PM program overdue.
33 | 21-90-ED-XT-TR2 | 14231662_3 | GEN | 1.6 | 6.6 | 0.4 | 6.6/0.4 | Auxiliary | 33 | 80 | Healthy | - | - | A | A | A | A | U | A | A | A | A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 04/01/2026 |  |  |  |  | 2019 | 2022 | 3Y PM program overdue.
34 | 21-90-ED-XT-TR3 | 14231662_1 | GEN | 1.6 | 6.6 | 0.4 | 6.6/0.4 | Auxiliary | 33 | 80 | Healthy | - | - | A | A | A | A | U | A | A | A | A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 04/01/2026 |  |  |  |  | 2019 | 2022 | 3Y PM program overdue.
35 | 21-90-ED-XT-TR4 | 14231662_4 | GEN | 1.6 | 6.6 | 0.4 | 6.6/0.4 | Auxiliary | 33 | 80 | Healthy | - | - | A | A | A | A | U | A | A | A | A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 04/01/2026 |  |  |  |  | 2019 | 2022 | 3Y PM program overdue.
35 | 61BBT01 (GH1 UAT1) | 3011080055 | GHECO-ONE | 60 | 23 | 11 | 23/11 | UAT | 16 | 86 | Healthy | 980 | 25 | [39 empty] | 2026 | - | Routine Inspection & Maintenance. | bar: A to A; N/A to N/A; Q to A; A to A
35 | 61BBT02 (GH1 UAT2) | 3011080056 | GHECO-ONE | 60 | 23 | 11 | 23/11 | UAT | 16 | 80 | Healthy | 980 | 25 | A | A | A | A | U | A | A | A | A |  | A | A |  |  |  | A | Q | A | A | A | A | A | A | A | A |  | Q | A | A | A | [9 empty] | 2019 | - | Routine Inspection & Maintenance.
35 | 61BBT03 (GH1 Excitation) | JD85034202 | GHECO-ONE | 7 | 23 | 0.92 | 23/0.92 | UAT | 16 | 74 | Monitor | 923 | 25 | A | A | A | A | U | A | A |  | A |  | A | A |  |  |  | A | Q | A | A | A | A | A | A | A | A |  | Q | A | A | A | [9 empty] | 2026 | - | Routine Inspection & Maintenance.
35 | 61BAT01 (GH1 GSUT) | TP70279703 | GHECO-ONE | 875 | 245 | 23 | 245/23 | GSUT | 16 | 85 | Healthy | 1031 | 25 | [39 empty] | 2026 | - | Routine Inspection & Maintenance. | bar: A to A; N/A to N/A; Q to A; A to A
35 | 61BMT03 (Back Up) | 5513053 | GHECO-ONE | 10 | 22 | 11 | 22/11 | Auxiliary | 14 | 78 | Monitor | 1117 | 25 | A | A | A | A | U | A | A | A | A |  | A | A |  |  |  | A | Q | A | A | A | A | A | A | A | A |  | Q | A | A | A | [9 empty] | 2025 | - | Routine Inspection & Maintenance.
35 | 61BFT01 (LV TR-1) | VN85040201_1 | GHECO-ONE | 2.5 | 10.5 | 0.4 | 10.5/0.4 | Auxiliary | 16 | 88 | Healthy | 950 | 25 | A: A; Q: A; A: A; U: A; A: U; A: A; Q: Q; U: A; A: A; N/A: A; N/A: A; Q: A; A: A; A: A; A: A | [5 empty] | 2019 | - | Routine Inspection & Maintenance.
35 | 61BFT02 (LV TR-2) | VN85040201_2 | GHECO-ONE | 2.5 | 10.5 | 0.4 | 10.5/0.4 | Auxiliary | 16 | 88 | Healthy | 950 | 25 | A: A; Q: A; A: A; U: A; A: U; A: A; Q: Q; U: A; A: A; N/A: A; N/A: A; Q: A; A: A; A: A; A: A | [5 empty] | 2019 | - | Routine Inspection & Maintenance.
35 | 61BFT03 (LV TR-3) | VN85040201_3 | GHECO-ONE | 2.5 | 10.5 | 0.4 | 10.5/0.4 | Auxiliary | 16 | 88 | Healthy | 950 | 25 | A: A; Q: A; A: A; U: A; A: U; A: A; Q: Q; U: A; A: A; N/A: A; N/A: A; Q: A; A: A; A: A; A: A | [5 empty] | 2019 | - | Routine Inspection & Maintenance.
35 | 61BFT04 (LV TR-4) | VN85040201_4 | GHECO-ONE | 2.5 | 10.5 | 0.4 | 10.5/0.4 | Auxiliary | 16 | 88 | Healthy | 950 | 25 | A: A; Q: A; A: A; U: A; A: U; A: A; Q: Q; U: A; A: A; N/A: A; N/A: A; Q: A; A: A; A: A; A: A | [5 empty] | 2019 | - | Routine Inspection & Maintenance.
35 | 61BFT05 (LV TR-5) | VN85040204_1 | GHECO-ONE | 2.5 | 10.5 | 0.4 | 10.5/0.4 | Auxiliary | 16 | 88 | Healthy | 950 | 25 | [39 empty] | 2019 | - | Routine Inspection & Maintenance. | bar: A to A; N/A to N/A; Q to A
35 | 61BFT06 (LV TR-6) | VN85040204_2 | GHECO-ONE | 2.5 | 10.5 | 0.4 | 10.5/0.4 | Auxiliary | 16 | 88 | Healthy | 950 | 25 | A: A; Q: A; A: A; U: A; A: U; A: A; Q: Q; U: A; A: A; N/A: A; N/A: A; Q: A; A: A; A: A; A: A | [5 empty] | 2019 | - | Routine Inspection & Maintenance.
35 | 61BGT01 (LV ESP-1) | VN85042301_1 | GHECO-ONE | 3.5 | 10.5 | 0.4 | 10.5/0.4 | Auxiliary | 16 | 88 | Healthy | 950 | 25 | [39 empty] | 2019 | - | Routine Inspection & Maintenance. | bar: A to A; N/A to N/A; Q to A
35 | 61BGT02 (LV ESP-2) | VN85042301_2 | GHECO-ONE | 3.5 | 10.5 | 0.4 | 10.5/0.4 | Auxiliary | 16 | 88 | Healthy | 950 | 25 | [39 empty] | 2019 | - | Routine Inspection & Maintenance. | bar: A to A; N/A to N/A; Q to A
35 | 61BGT09 (LV SWFGD-1) | VN85040202_1 | GHECO-ONE | 1.5 | 10.5 | 0.4 | 10.5/0.4 | Auxiliary | 16 | 88 | Healthy | 950 | 25 | A: A; Q: A; A: A; U: A; A: U; A: A; Q: Q; U: A; A: A; N/A: A; N/A: A; Q: A; A: A; A: A; A: A | [5 empty] | 2019 | - | Routine Inspection & Maintenance.
35 | 61BGT10 (LV SWFGD-2) | VN85040202_2 | GHECO-ONE | 1.5 | 10.5 | 0.4 | 10.5/0.4 | Auxiliary | 16 | 88 | Healthy | 950 | 25 | A: A; Q: A; A: A; U: A; A: U; A: A; Q: Q; U: A; A: A; N/A: A; N/A: A; Q: A; A: A; A: A; A: A | [5 empty] | 2019 | - | Routine Inspection & Maintenance.
35 | 61BGT07 (LV ASH-1) | VN85042302_2 | GHECO-ONE | 1.5 | 10.5 | 0.4 | 10.5/0.4 | Auxiliary | 16 | 84 | Healthy | 950 | 25 | A: A; Q: A; A: A; U: Q; A: U; A: A; Q: A; U: A; A: A; N/A: A; N/A: A; Q: A; A: A; A: A; A: A | [5 empty] | 2019 | - | Routine Inspection & Maintenance.
35 | 61BGT08 (LV ASH-2) | VN85042302_1 | GHECO-ONE | 1.5 | 10.5 | 0.4 | 10.5/0.4 | Auxiliary | 16 | 84 | Healthy | 950 | 25 | [39 empty] | 2019 | - | Routine Inspection & Maintenance. | bar: A to A; N/A to N/A; Q to A
35 | 61BGT05 (LV CHS-1) | VN13700702_2 | GHECO-ONE | 1 | 10.5 | 0.4 | 10.5/0.4 | Auxiliary | 16 | 88 | Healthy | 950 | 25 | A: A; Q: A; A: A; U: U; A: U; A: A; Q: Q; U: A; A: A; N/A: A; N/A: A; Q: A; A: A; A: A; A: A | [5 empty] | 2019 | - | Routine Inspection & Maintenance.
35 | 61BGT06 (LV CHS-2) | VN13700702_1 | GHECO-ONE | 1 | 10.5 | 0.4 | 10.5/0.4 | Auxiliary | 16 | 88 | Healthy | 950 | 25 | A: A; Q: A; A: A; U: A; A: U; A: A; Q: Q; U: A; A: A; N/A: A; N/A: A; Q: A; A: A; A: A; A: A | [5 empty] | 2019 | - | Routine Inspection & Maintenance.
35 | 61BGT03 (LV CHS-3) | VN13700701_2 | GHECO-ONE | 1.5 | 10.5 | 0.4 | 10.5/0.4 | Auxiliary | 16 | 84 | Healthy | 950 | 25 | [39 empty] | 2019 | - | Routine Inspection & Maintenance. | bar: A to A; N/A to N/A; Q to A
35 | 61BGT04 (LV CHS-4) | VN13700701_1 | GHECO-ONE | 1.5 | 10.5 | 0.4 | 10.5/0.4 | Auxiliary | 16 | 88 | Healthy | 950 | 25 | [39 empty] | 2019 | - | Routine Inspection & Maintenance. | bar: A to A; N/A to N/A; Q to A
35 | 61GBY01GT001.35.EN | 170709/1 | GHECO-ONE | 1.17 | 10.5 | 0.15 | 10.5/0.15 | Auxiliary | 16 | 100 | Healthy | 950 | 25 | [39 empty] | 2025 | - | Routine Inspection & Maintenance. | bar: A to Q; N/A to N/A; Q to A
35 | 61GBY01GT002.35.EN | 170709/2 | GHECO-ONE | 1.17 | 10.5 | 0.15 | 10.5/0.15 | Auxiliary | 16 | 100 | Healthy | 950 | 25 | [39 empty] | 2025 | - | Routine Inspection & Maintenance. | bar: A to Q; N/A to N/A; Q to A
35 | 61HDE10GT001.35.EN | N09057 | GHECO-ONE | 0.136 | 0.4 | 0.11 | 0.4/0.11 | Auxiliary | - | 100 | Healthy | 950 | 25 | [39 empty] | 2025 | - | Routine Inspection & Maintenance. | bar: A to Q; N/A to N/A; Q to A
35 | 61HDE10GT002.35.EN | N09058 | GHECO-ONE | 0.136 | 0.4 | 0.11 | 0.4/0.11 | Auxiliary | - | 100 | Healthy | 950 | 25 | [39 empty] | 2025 | - | Routine Inspection & Maintenance. | bar: A to Q; N/A to N/A; Q to A
35 | 61HDE10GT003.35.EN | N09059 | GHECO-ONE | 0.136 | 0.4 | 0.11 | 0.4/0.11 | Auxiliary | - | 100 | Healthy | 950 | 25 | [39 empty] | 2025 | - | Routine Inspection & Maintenance. | bar: A to Q; N/A to N/A; Q to A
35 | 61HDE10GT004.35.EN | N09060 | GHECO-ONE | 0.136 | 0.4 | 0.11 | 0.4/0.11 | Auxiliary | - | 100 | Healthy | 950 | 25 | [39 empty] | 2025 | - | Routine Inspection & Maintenance. | bar: A to Q; N/A to N/A; Q to A
35 | 61HDE10GT005.35.EN | N09061 | GHECO-ONE | 0.136 | 0.4 | 0.11 | 0.4/0.11 | Auxiliary | - | 100 | Healthy | 950 | 25 | [39 empty] | 2025 | - | Routine Inspection & Maintenance. | bar: A to Q; N/A to N/A; Q to A
35 | 61HDE10GT006.35.EN | N09062 | GHECO-ONE | 0.136 | 0.4 | 0.11 | 0.4/0.11 | Auxiliary | - | 100 | Healthy | 950 | 25 | [39 empty] | 2025 | - | Routine Inspection & Maintenance. | bar: A to Q; N/A to N/A; Q to A
35 | 61HDE10GT007.35.EN | N09063 | GHECO-ONE | 0.136 | 0.4 | 0.11 | 0.4/0.11 | Auxiliary | - | 100 | Healthy | 950 | 25 | [39 empty] | 2025 | - | Routine Inspection & Maintenance. | bar: A to Q; N/A to N/A; Q to A
35 | 61HDE10GT008.35.EN | N09064 | GHECO-ONE | 0.136 | 0.4 | 0.11 | 0.4/0.11 | Auxiliary | - | 100 | Healthy | 950 | 25 | [39 empty] | 2025 | - | Routine Inspection & Maintenance. | bar: A to Q; N/A to N/A; Q to A
35 | 61HDE10GT009.35.EN | N09065 | GHECO-ONE | 0.136 | 0.4 | 0.11 | 0.4/0.11 | Auxiliary | - | 100 | Healthy | 950 | 25 | [39 empty] | 2025 | - | Routine Inspection & Maintenance. | bar: A to Q; N/A to N/A; Q to A
35 | 61HDE10GT010.35.EN | N09066 | GHECO-ONE | 0.136 | 0.4 | 0.11 | 0.4/0.11 | Auxiliary | - | 100 | Healthy | 950 | 25 | [39 empty] | 2025 | - | Routine Inspection & Maintenance. | bar: A to Q; N/A to N/A; Q to A
35 | 61HDE10GT011.35.EN | N09067 | GHECO-ONE | 0.136 | 0.4 | 0.11 | 0.4/0.11 | Auxiliary | - | 100 | Healthy | 950 | 25 | [39 empty] | 2025 | - | Routine Inspection & Maintenance. | bar: A to Q; N/A to N/A; Q to A
35 | 61HDE10GT012.35.EN | N09068 | GHECO-ONE | 0.136 | 0.4 | 0.11 | 0.4/0.11 | Auxiliary | - | 100 | Healthy | 950 | 25 | [39 empty] | 2025 | - | Routine Inspection & Maintenance. | bar: A to Q; N/A to N/A; Q to A
35 | 61HDE20GT001.35.EN | N09069 | GHECO-ONE | 0.136 | 0.4 | 0.11 | 0.4/0.11 | Auxiliary | - | 100 | Healthy | 950 | 25 | [39 empty] | 2025 | - | Routine Inspection & Maintenance. | bar: A to Q; N/A to N/A; Q to A
35 | 61HDE20GT002.35.EN | N09070 | GHECO-ONE | 0.136 | 0.4 | 0.11 | 0.4/0.11 | Auxiliary | - | 100 | Healthy | 950 | 25 | [39 empty] | 2025 | - | Routine Inspection & Maintenance. | bar: A to Q; N/A to N/A; Q to A
35 | 61HDE20GT003.35.EN | N09071 | GHECO-ONE | 0.136 | 0.4 | 0.11 | 0.4/0.11 | Auxiliary | - | 100 | Healthy | 950 | 25 | [39 empty] | 2025 | - | Routine Inspection & Maintenance. | bar: A to Q; N/A to N/A; Q to A
35 | 61HDE20GT004.35.EN | N09072 | GHECO-ONE | 0.136 | 0.4 | 0.11 | 0.4/0.11 | Auxiliary | - | 100 | Healthy | 950 | 25 | [39 empty] | 2025 | - | Routine Inspection & Maintenance. | bar: A to Q; N/A to N/A; Q to A
35 | 61HDE20GT005.35.EN | N09073 | GHECO-ONE | 0.136 | 0.4 | 0.11 | 0.4/0.11 | Auxiliary | - | 100 | Healthy | 950 | 25 | [39 empty] | 2025 | - | Routine Inspection & Maintenance. | bar: A to Q; N/A to N/A; Q to A
35 | 61HDE20GT006.35.EN | N09074 | GHECO-ONE | 0.136 | 0.4 | 0.11 | 0.4/0.11 | Auxiliary | - | 100 | Healthy | 950 | 25 | [39 empty] | 2025 | - | Routine Inspection & Maintenance. | bar: A to Q; N/A to N/A; Q to A
35 | 61HDE20GT007.35.EN | N09075 | GHECO-ONE | 0.136 | 0.4 | 0.11 | 0.4/0.11 | Auxiliary | - | 100 | Healthy | 950 | 25 | [39 empty] | 2025 | - | Routine Inspection & Maintenance. | bar: A to Q; N/A to N/A; Q to A
35 | 61HDE20GT008.35.EN | N09076 | GHECO-ONE | 0.136 | 0.4 | 0.11 | 0.4/0.11 | Auxiliary | - | 100 | Healthy | 950 | 25 | [39 empty] | 2025 | - | Routine Inspection & Maintenance. | bar: A to Q; N/A to N/A; Q to A
35 | 61HDE20GT009.35.EN | N09077 | GHECO-ONE | 0.136 | 0.4 | 0.11 | 0.4/0.11 | Auxiliary | - | 100 | Healthy | 950 | 25 | [39 empty] | 2025 | - | Routine Inspection & Maintenance. | bar: A to Q; N/A to N/A; Q to A
35 | 61HDE20GT010.35.EN | N09078 | GHECO-ONE | 0.136 | 0.4 | 0.11 | 0.4/0.11 | Auxiliary | - | 100 | Healthy | 950 | 25 | [39 empty] | 2025 | - | Routine Inspection & Maintenance. | bar: A to Q; N/A to N/A; Q to A
35 | 61HDE20GT011.35.EN | N09079 | GHECO-ONE | 0.136 | 0.4 | 0.11 | 0.4/0.11 | Auxiliary | - | 100 | Healthy | 950 | 25 | [39 empty] | 2025 | - | Routine Inspection & Maintenance. | bar: A to Q; N/A to N/A; Q to A
35 | 61HDE20GT012.35.EN | N09080 | GHECO-ONE | 0.136 | 0.4 | 0.11 | 0.4/0.11 | Auxiliary | - | 100 | Healthy | 950 | 25 | [39 empty] | 2025 | - | Routine Inspection & Maintenance. | bar: A to Q; N/A to N/A; Q to A
35 | 11BBT20 | T013001 | GIPP | 40 | 21 | 6.75 | 21/6.75 | UAT | 25 | 90 | Healthy | 1152 | 25 | [39 empty] | 2025 | - | Routine Inspection & Maintenance. | bar: A to Q; N/A to N/A; Q to A; A to A
35 | 21BBT20 | T013007 | GIPP | 40 | 21 | 6.75 | 21/6.75 | UAT | 25 | 85 | Healthy | 1152 | 25 | [39 empty] | 2025 | - | Routine Inspection & Maintenance. | bar: A to Q; N/A to N/A; Q to A; A to A
35 | 11BAT10 | T012006 | GIPP | 500 | 235 | 121 | 235/121 | GSUT | 25 | 80 | Healthy | 1003 | 25 | A | A | A | A | A | A | A | A | U |  | A | A |  |  |  | A | Q | A | A | A | A | A | A | A | A |  | A | Q | A | A | [9 empty] | 2026 | - | Routine Inspection & Maintenance.
35 | 21BAT10 | T012023 | GIPP | 500 | 235 | 121 | 235/121 | GSUT | 25 | 80 | Healthy | 1003 | 25 | [39 empty] | 2025 | - | Routine Inspection & Maintenance. | bar: A to Q; N/A to N/A; Q to A; A to A
35 | 11MKC50 (Excitation) | 5217613 | GIPP | 4.1 | 21 | 0.52 | 21/0.52 | Auxiliary | 25 | 79 | Monitor | 1003 | 25 | [39 empty] | 2025 | - | Routine Inspection & Maintenance. | bar: A to Q; N/A to N/A; Q to A; A to A
35 | 21MKC50 (Excitation) | 5217612 | GIPP | 4.1 | 21 | 0.52 | 21/0.52 | Auxiliary | 25 | 79 | Monitor | 1003 | 25 | [39 empty] | 2025 | - | Routine Inspection & Maintenance. | bar: A to Q; N/A to N/A; Q to A; A to A
35 | 11BFT10 | 424758_03 | GIPP | 2.5 | 6.6 | 0.4 | 6.6/0.4 | Auxiliary | 25 | 0 | Critical | 950 | 25 | [39 empty] | 2025 | - | Routine Inspection & Maintenance. | bar: A to Q; N/A to N/A; Q to A
35 | 11BFT20 | 424758_04 | GIPP | 2.5 | 6.6 | 0.4 | 6.6/0.4 | Auxiliary | 25 | 0 | Critical | 950 | 25 | [39 empty] | 2025 | - | Routine Inspection & Maintenance. | bar: A to Q; N/A to N/A; Q to A
35 | 11BFT30 | 424759_01 | GIPP | 2.5 | 6.6 | 0.4 | 6.6/0.4 | Auxiliary | 25 | 0 | Critical | 950 | 25 | [39 empty] | 2025 | - | Routine Inspection & Maintenance. | bar: A to Q; N/A to N/A; Q to A
35 | 21BFT10 | 424758_01 | GIPP | 2.5 | 6.6 | 0.4 | 6.6/0.4 | Auxiliary | 25 | 0 | Critical | 950 | 25 | [39 empty] | 2025 | - | Routine Inspection & Maintenance. | bar: A to Q; N/A to N/A; Q to A
35 | 21BFT20 | 424759_02 | GIPP | 2.5 | 6.6 | 0.4 | 6.6/0.4 | Auxiliary | 25 | 0 | Critical | 950 | 25 | [39 empty] | 2025 | - | Routine Inspection & Maintenance. | bar: A to Q; N/A to N/A; Q to A
35 | 21BFT30 | 424758_02 | GIPP | 2.5 | 6.6 | 0.4 | 6.6/0.4 | Auxiliary | 25 | 0 | Critical | 950 | 25 | [39 empty] | 2025 | - | Routine Inspection & Maintenance. | bar: A to Q; N/A to N/A; Q to A
35 | TR-1501 | EV9277_1 | GSPP11 PLT1 | 4.75 | 11 | 6.9 | 11/6.9 | UAT | 26 | 90 | Healthy | 855 | 25 | [39 empty] | 2025 | - | Routine Inspection & Maintenance. | bar: A to Q; N/A to N/A; Q to A; A to A
35 | TR-1502 | EV9277_2 | GSPP11 PLT1 | 4.75 | 11 | 6.9 | 11/6.9 | UAT | 26 | 85 | Healthy | 923 | 25 | [39 empty] | 2025 | - | Routine Inspection & Maintenance. | bar: A to Q; N/A to N/A; Q to A; A to A
35 | TR-101 | ET8712/1 | GSPP11 PLT1 | 48 | 123 | 11 | 123/11 | GSUT | 27 | 80 | Healthy | 923 | 25 | A | A | A | U | A | A | A | A | A |  | A | A |  |  |  | A | Q | A | A | A | Q | A | A | A | A |  | A | Q | A | A | [9 empty] | 2023 | - | Routine Inspection & Maintenance.
35 | TR-201 | ET8712_2 | GSPP11 PLT1 | 48 | 123 | 11 | 123/11 | GSUT | 33 | 68 | Warning | 961 | 25 | [39 empty] | 2024 | - | Routine Inspection & Maintenance. | bar: A to A; N/A to N/A; Q to A; A to A
35 | TR-301 | ET8713/1 | GSPP11 PLT1 | 52 | 123 | 10.5 | 123/10.5 | GSUT | 27 | 80 | Healthy | 1003 | 25 | [39 empty] | 2023 | - | Routine Inspection & Maintenance. | bar: A to A; N/A to N/A; Q to A; A to A
35 | GE-TR1 | PP0091B01 | GSPP11 PLT1 | 26 | 22 | 11 | 22/11 | GSUT | 20 | 90 | Healthy | 1047 | 25 | [39 empty] | 2025 | - | Routine Inspection & Maintenance. | bar: A to Q; N/A to N/A; Q to A; A to A
35 | GE-TR2 | 5710877 | GSPP11 PLT1 | 25 | 22 | 11 | 22/11 | GSUT | 12 | 80 | Healthy | 1066 | 25 | [39 empty] | 2025 | - | Routine Inspection & Maintenance. | bar: A to Q; N/A to N/A; Q to A; A to A
35 | TR-401 | EDP004301 | GSPP11 PLT1 | 25 | 115 | 22 | 115/22 | Distribution | 31 | 83 | Healthy | 796 | 25 | [39 empty] | 2018 | - | Routine Inspection & Maintenance. | bar: A to A; N/A to N/A; Q to A; A to A
35 | TR-501 | EDP018401 | GSPP11 PLT1 | 25 | 115 | 22 | 115/22 | Distribution | 25 | 85 | Healthy | 980 | 25 | [39 empty] | 2023 | - | Routine Inspection & Maintenance. | bar: A to A; N/A to N/A; Q to A; A to A
35 | TR-601 | PP0041B01 | GSPP11 PLT1 | 20 | 115 | 22 | 115/22 | Distribution | 22 | 80 | Healthy | 905 | 25 | [39 empty] | 2025 | - | Routine Inspection & Maintenance. | bar: A to Q; N/A to N/A; Q to A; A to A
35 | TR-40001 | 4700831 | GSPP11 PLT1 | 2.5 | 22 | 0.4 | 22/0.4 | Auxiliary | 22 | 91 | Healthy | 937 | 25 | [39 empty] | 2018 | - | Routine Inspection & Maintenance. | bar: A to Q; N/A to N/A; Q to A; A to A
35 | TR-40002 | 4700830 | GSPP11 PLT1 | 2.5 | 22 | 0.4 | 22/0.4 | Auxiliary | 22 | 80 | Healthy | 847 | 25 | [39 empty] | 2018 | - | Routine Inspection & Maintenance. | bar: A to Q; N/A to N/A; Q to A; A to A
35 | GE-TR1 Aux. | O61539 | GSPP11 PLT1 | 1.25 | 11 | 0.4 | 11/0.4 | Auxiliary | 20 | 100 | Healthy | 911 | 25 | [39 empty] | 2025 | - | Routine Inspection & Maintenance. | bar: A to Q; N/A to N/A; Q to A; A to A
35 | GE-TR2 Aux. | 5710876 | GSPP11 PLT1 | 0.63 | 11 | 0.4 | 11/0.4 | Auxiliary | 12 | 49 | Critical | 1200 | 25 | A | A | A | A | A | A | A |  |  |  | A | A |  |  |  | A | U | Q | A | A | A | A | A | Q | A |  | Q | Q | A | Q | [9 empty] | 2025 | - | Routine Inspection & Maintenance.
35 | GSUT-1 | PP0284B01 | GSPP11 PLT2 | 90 | 115 | 11 | 115/11 | GSUT | 15 | 90 | Healthy | 950 | 25 | [39 empty] | 2025 | - | Routine Inspection & Maintenance. | bar: A to Q; N/A to N/A; Q to A; A
35 | GSUT-2 | PP0285B01 | GSPP11 PLT2 | 55 | 115 | 11 | 115/11 | GSUT | 15 | 100 | Healthy | 950 | 25 | [39 empty] | 2025 | - | Routine Inspection & Maintenance. | bar: A to Q; N/A to N/A; Q to A; A
35 | DT-3 | 56016 | GSPP11 PLT2 | 50 | 115 | 22 | 115/22 | Distribution | 30 | 88 | Healthy | 1003 | 25 | [39 empty] | 2025 | - | Routine Inspection & Maintenance. | bar: A to A; N/A to N/A; Q to A; A to A
35 | SST-1 | 54110640EE | GSPP11 PLT2 | 6.25 | 11 | 3.3 | 11/3.3 | Auxiliary | 15 | 90 | Healthy | 950 | 25 | [39 empty] | 2025 | - | Routine Inspection & Maintenance. | bar: A to Q; N/A to N/A; Q to A; A
35 | SST-2 | 54110641EE | GSPP11 PLT2 | 6.25 | 11 | 3.3 | 11/3.3 | Auxiliary | 15 | 90 | Healthy | 950 | 25 | [39 empty] | 2025 | - | Routine Inspection & Maintenance. | bar: A to Q; N/A to N/A; Q to A; A
35 | SAT-1 | 54110621EE | GSPP11 PLT2 | 2.3 | 11 | 0.4 | 11/0.4 | Auxiliary | 15 | 90 | Healthy | 950 | 25 | [39 empty] | 2025 | - | Routine Inspection & Maintenance. | bar: A to Q; N/A to N/A; Q to A; A
35 | SAT-2 | 54110620EE | GSPP11 PLT2 | 2.3 | 11 | 0.4 | 11/0.4 | Auxiliary | 15 | 100 | Healthy | 950 | 25 | [39 empty] | 2025 | - | Routine Inspection & Maintenance. | bar: A to Q; N/A to N/A; Q to A; A
36 | COGEN UAT | 9624007 | GSPP2&3 | 13.4 | 11.5 | 7.2 | 11.5/7.2 | UAT | 30 | 80 | Healthy | 880 | 25 | A | A | A | A | U | A | A | A | A |  | A | A |  |  |  | A | Q | A | A | A | A | A | A | A | A |  | A | A | A | Q | [9 empty] | 2024 | - | Routine Inspection & Maintenance.
37 | STG3C UAT | 5011858 | GSPP2&3 | 20 | 15.75 | 7.2 | 15.75/7.2 | UAT | 18 | 93 | Healthy | 961 | 25 | [39 empty] | 2021 | - | Routine Inspection & Maintenance. | bar: A to A; N/A to N/A; Q to A; A to A
38 | 71BBT10 (CTG7A UAT) | 225307 | GSPP2&3 | 8 | 11 | 6.9 | 11/6.9 | UAT | 3 | 85 | Healthy | 1117 | 25 | A | A | A | A | A | A | A | A | U |  | A | A |  |  |  | A | A | A | A | A | A | A | A | A | A |  | Q | A | A | A | [9 empty] | 2023 | - | Routine Inspection & Maintenance.
39 | 72BBT10 (CTG7B UAT) | 225308 | GSPP2&3 | 8 | 11 | 6.9 | 11/6.9 | UAT | 3 | 90 | Healthy | 1089 | 25 | [39 empty] | 2025 | - | Routine Inspection & Maintenance. | bar: A to Q; N/A to N/A; Q to A; A to A
40 | STG1C UAT | 9724074 | GSPP2&3 | 22.4 | 15.75 | 7.2 | 15.75/7.2 | UAT | 28 | 83 | Healthy | 745 | 25 | A | A | A | U | U | A | A | A | A |  | A | A |  |  |  | A | Q | A | A | A | A | A | A | A | A |  | A | A | A | A | [9 empty] | 2018 | - | Routine Inspection & Maintenance.
41 | STG2C UAT1 | 9724076 | GSPP2&3 | 22.4 | 11.5 | 7.2 | 11.5/7.2 | UAT | 28 | 65 | Warning | 859 | 25 | Q | A | A | A | U | A | A | A | A |  | A | A |  |  |  | A | Q | A | A | A | A | A | A | A | A |  | A | A | A | A | [9 empty] | 2019 | - | Routine Inspection & Maintenance.
42 | STG2C UAT2 | 9724075 | GSPP2&3 | 22.4 | 15.75 | 7.2 | 15.75/7.2 | UAT | 28 | 90 | Healthy | 917 | 25 | [39 empty] | 2023 | - | Routine Inspection & Maintenance. | bar: A to A; N/A to N/A; Q to A; A to A
43 | 31BBT10 (CTG3A UAT) | 4711343 | GSPP2&3 | 2 | 11.5 | 7.2 | 11.5/7.2 | UAT | 21 | 88 | Healthy | 970 | 25 | [39 empty] | 2024 | - | Routine Inspection & Maintenance. | bar: A to A; N/A to N/A; Q to A; A to A
44 | 32BBT10 (CTG3B UAT) | 4612314 | GSPP2&3 | 2 | 11.5 | 7.2 | 11.5/7.2 | UAT | 22 | 65 | Warning | 1066 | 25 | [39 empty] | 2018 | - | Routine Inspection & Maintenance. | bar: A to U; N/A to N/A; Q to A; A to A
45 | 51BBT01 (CTG5 GSUT) | VN00408 | GSPP2&3 | 20 | 20 | 6.9 | 20/6.9 | UAT | 17 | 89 | Healthy | 1003 | 25 | [39 empty] | 2025 | - | Routine Inspection & Maintenance. | bar: A to A; N/A to N/A; Q to A; A to A
46 | COGEN GSUT (CTG1&2) | 9640548 | GSPP2&3 | 90 | 118 | 11.5/11.5 | 118/11.5/11.5 | GSUT | 30 | 75 | Monitor | 781 | 25 | [39 empty] | 2024 | - | Routine Inspection & Maintenance. | bar: A to A; N/A to N/A; Q to A; A to A
47 | CTG1A&1B GSUT | 9640549 | GSPP2&3 | 90 | 118 | 11.5/11.5 | 118/11.5/11.5 | GSUT | 30 | 77 | Monitor | 785 | 25 | [39 empty] | 2023 | - | Routine Inspection & Maintenance. | bar: A to A; N/A to N/A; Q to A; A to A
48 | CTG2A&2B GSUT | 57005 | GSPP2&3 | 90 | 118 | 11.5/11.5 | 118/11.5/11.5 | GSUT | 29 | 83 | Healthy | 871 | 25 | [39 empty] | 2022 | - | Routine Inspection & Maintenance. | bar: A to A; N/A to N/A; Q to A; A to A
49 | STG3C GSUT | 5011857 | GSPP2&3 | 155 | 118 | 15.75 | 118/15.75 | GSUT | 18 | 93 | Healthy | 930 | 25 | [39 empty] | 2024 | - | Routine Inspection & Maintenance. | bar: A to A; N/A to N/A; Q to A; A to A
50 | 71BAT10 (CTG7A GSUT) | 6512362 | GSPP2&3 | 72 | 118 | 11 | 118/11 | GSUT | 3 | 88 | Healthy | 1089 | 25 | [39 empty] | 2023 | - | Routine Inspection & Maintenance. | bar: A to U; N/A to N/A; Q to A; A to A
51 | 72BAT10 (CTG7B GSUT) | 6512363 | GSPP2&3 | 72 | 118 | 11 | 118/11 | GSUT | 3 | 80 | Healthy | 1117 | 25 | A | A | A | A | U | A | A | A | U |  | A | A |  |  |  | A | Q | A | A | A | A | A | A | A | A |  | Q | A | A | A | [9 empty] | 2023 | - | Routine Inspection & Maintenance.
52 | STG1C GSUT | 57011 | GSPP2&3 | 215 | 118 | 15.75 | 118/15.75 | GSUT | 29 | 80 | Healthy | 620 | 25 | A | A | A | A | U | A | Q | A | A |  | A | A |  |  |  | A | Q | A | A | A | A | A | A | A | A |  | A | Q | A | A | [9 empty] | 2025 | - | Routine Inspection & Maintenance.
53 | STG2C GSUT | 57012 | GSPP2&3 | 215 | 118 | 15.75 | 118/15.75 | GSUT | 29 | 86 | Healthy | 917 | 25 | [39 empty] | 2019 | - | Routine Inspection & Maintenance. | bar: A to A; N/A to N/A; Q to A; A to A
54 | 31BAT10 (CTG3A GSUT) | PP0050B01 | GSPP2&3 | 51.5 | 118 | 11.5 | 118/11.5 | GSUT | 21 | 78 | Monitor | 806 | 25 | A | A | A | A | U | A | A | A | A |  | A | A |  |  |  | A | Q | A | A | A | A | A | A | A | A |  | A | Q | A | A | [9 empty] | 2024 | - | Routine Inspection & Maintenance.
55 | 32BAT10 (CTG3B GSUT) | PP0016B01 | GSPP2&3 | 51.5 | 118 | 11.5 | 118/11.5 | GSUT | 22 | 90 | Healthy | 930 | 25 | [39 empty] | 2026 | - | Routine Inspection & Maintenance. | bar: A to A; N/A to N/A; Q to A; A to A
56 | 50BAT10 (CTG5 GSUT) | 20083122TIC003 | GSPP2&3 | 325 | 115 | 20 | 115/20 | GSUT | 16 | 65 | Warning | 953 | 25 | [39 empty] | 2025 | - | Routine Inspection & Maintenance. | bar: A to A; N/A to N/A; Q to A; A to A
57 | 52BAT01 (STG5 GSUT) | 20083122TIC008 | GSPP2&3 | 175 | 115 | 15.75 | 115/15.75 | GSUT | 16 | 95 | Healthy | 980 | 25 | [39 empty] | 2025 | - | Routine Inspection & Maintenance. | bar: A to A; N/A to N/A; Q to A; A to A
58 | KT2A | 510049 | GSPP2&3 | 200 | 230 | 121 | 230/121 | Distribution | 15 | 70 | Monitor | 980 | 25 | [39 empty] | 2025 | - | Routine Inspection & Maintenance. | bar: A to A; N/A to N/A; Q to A; A to A
59 | KT4A | PTE 1689/01 | GSPP2&3 | 200 | 230 | 121 | 230/121 | Distribution | 28 | 85 | Healthy | 1066 | 25 | [39 empty] | 2024 | - | Routine Inspection & Maintenance. | bar: A to A; N/A to N/A; Q to A; A to A
60 | KT5A | PTE 1689/02 | GSPP2&3 | 200 | 230 | 121 | 230/121 | Distribution | 28 | 90 | Healthy | 1066 | 25 | [39 empty] | 2025 | - | Routine Inspection & Maintenance. | bar: A to A; N/A to N/A; Q to A; A to A
61 | KT6A | PTE 1689/03 | GSPP2&3 | 200 | 230 | 121 | 230/121 | Distribution | 28 | 80 | Healthy | 970 | 25 | A | A | A | A | A | A | A | A | A |  | A | U |  |  |  | A | Q | A | A | A | A | A | A | A | A |  | A | A | A | A | [9 empty] | 2025 | - | Routine Inspection & Maintenance.
62 | KT7A | PTE 1689/04 | GSPP2&3 | 200 | 230 | 121 | 230/121 | Distribution | 28 | 73 | Monitor | 917 | 25 | Q | A | A | A | A | A | A | A | A |  | A | U |  |  |  | A | A | A | A | A | A | A | A | A | A |  | A | A | A | A | [9 empty] | 2025 | - | Routine Inspection & Maintenance.
63 | KT12A | EDP008001 | GSPP2&3 | 50 | 112.5 | 23 | 112.5/23 | Distribution | 30 | 75 | Monitor | 961 | 25 | A | A | A | U | A | A | A | A | A |  | A | U |  |  |  | A | A | A | A | A | A | A | A | A | A |  | Q | Q | A | A | [9 empty] | 2025 | - | Routine Inspection & Maintenance.
64 | KT13A | EDP011601 | GSPP2&3 | 50 | 112.5 | 23 | 112.5/23 | Distribution | 28 | 75 | Monitor | 953 | 25 | A | A | A | U | A | A | A | A | A |  | A | U |  |  |  | A | Q | A | A | A | A | A | A | A | A |  | A | A | A | A | [9 empty] | 2024 | - | Routine Inspection & Maintenance.
65 | KT14A | 512033 | GSPP2&3 | 50 | 112.5 | 23 | 112.5/23 | Distribution | 14 | 73 | Monitor | 1066 | 25 | A | A | A | U | A | A | A | A | A |  | A | Q |  |  |  | A | Q | A | A | A | A | A | A | A | A |  | Q | A | A | A | [9 empty] | 2024 | - | Routine Inspection & Maintenance.
66 | CTG1 Aux. | PBE0580 | GSPP2&3 | 1.15 | 11.5 | 0.4 | 11.5/0.4 | Auxiliary | 30 | 49 | Critical | 1200 | 25 | A | A | A | A | Q | A | A | Q |  |  | A | A |  |  |  | A | U | Q | U | A | A | A | A | Q | A |  | Q | Q | A | A | [9 empty] | 2018 | - | Routine Inspection & Maintenance.
67 | CTG2 Aux. | PBE0579 | GSPP2&3 | 1.15 | 11.5 | 0.4 | 11.5/0.4 | Auxiliary | 29 | 49 | Critical | 950 | 25 | A | A | A | A | Q | A | A | Q |  |  | A | A |  |  |  | A | U | Q | U | A | A | A | A | A | A |  | A | A | A | A | [9 empty] | 2018 | - | Routine Inspection & Maintenance.
68 | COGEN SUS11 | 243597801 | GSPP2&3 | 2 | 6.9 | 0.4 | 6.9/0.4 | Auxiliary | 30 | 64 | Warning | 950 | 25 | [39 empty] | 2018 | - | Routine Inspection & Maintenance. | bar: A to Q; A; N/A to N/A; Q to A
69 | COGEN SUS12 | 243597802 | GSPP2&3 | 2 | 6.9 | 0.4 | 6.9/0.4 | Auxiliary | 29 | 60 | Warning | 950 | 25 | A: Q; Q: A; A: A; U: Q; A: A; A: A; Q: Q; U: U; A: A; N/A: A; N/A: A; Q: A; A: A; A: A; A: A | [5 empty] | 2018 | - | Routine Inspection & Maintenance.
70 | CTG1A Aux. | PBJ1200 | GSPP2&3 | 1.15 | 11.5 | 0.4 | 11.5/0.4 | Auxiliary | 30 | 83 | Healthy | 950 | 25 | A | A | A | A | U | A | Q | A | A |  | A | A |  |  |  | A | Q | A | A | A | A | A | A | A | A |  | A | A | A | A | [9 empty] | 2018 | - | Routine Inspection & Maintenance.
71 | CTG1B Aux. | PBJ1198 | GSPP2&3 | 1.15 | 11.5 | 0.4 | 11.5/0.4 | Auxiliary | 30 | 86 | Healthy | 1047 | 25 | A | A | A | A | U | A | A | Q |  |  | A | A |  |  |  | A | Q | A | A | A | A | A | A | A | A |  | A | A | A | A | [9 empty] | 2017 | - | Routine Inspection & Maintenance.
72 | CTG2A Aux. | PBK1325 | GSPP2&3 | 1.15 | 11.5 | 0.4 | 11.5/0.4 | Auxiliary | 29 | 80 | Healthy | 950 | 25 | A: A; Q: A; A: A; U: U; A: U; A: A; Q: Q; U: U; A: A; N/A: A; N/A: A; Q: A; A: Q; A: A; A: A; A: A | [5 empty] | 2017 | - | Routine Inspection & Maintenance.
73 | CTG2B Aux. | PBL1465 | GSPP2&3 | 1.15 | 11.5 | 0.4 | 11.5/0.4 | Auxiliary | 29 | 86 | Healthy | 674 | 25 | A | A | A | U | U | A | Q | Q | A |  | A | A |  |  |  | A | A | A | A | A | A | A | A | A | A |  | A | A | A | A | [9 empty] | 2025 | - | Routine Inspection & Maintenance.
74 | KW1A | 3911888 | GSPP2&3 | 0.5 | 22 | 0.4 | 22/0.4 | Auxiliary | 30 | 70 | Monitor | 917 | 25 | [39 empty] | 2022 | - | Routine Inspection & Maintenance. | bar: A to A; N/A to N/A; Q to A; A to A
75 | KW2A | 4010922 | GSPP2&3 | 0.5 | 22 | 0.4 | 22/0.4 | Auxiliary | 28 | 66 | Warning | 991 | 25 | Q | A | A | A | U | A | A | A | A |  | A | A |  |  |  | A | Q | A | A | A | A | A | A | A | A |  | A | A | A | A | [9 empty] | 2019 | - | Routine Inspection & Maintenance.
76 | KW3A | 4010291 | GSPP2&3 | 0.5 | 22 | 0.4 | 22/0.4 | Auxiliary | 28 | 90 | Healthy | 709 | 25 | [39 empty] | 2022 | - | Routine Inspection & Maintenance. | bar: A to A; N/A to N/A; Q to A; A to A
77 | KW4A | 4010290 | GSPP2&3 | 0.5 | 22 | 0.4 | 22/0.4 | Auxiliary | 28 | 95 | Healthy | 755 | 25 | [39 empty] | 2022 | - | Routine Inspection & Maintenance. | bar: A to A; N/A to N/A; Q to A; A to A
78 | KW5A | 5513260 | GSPP2&3 | 0.5 | 22 | 0.4 | 22/0.4 | Auxiliary | 13 | 77 | Monitor | 1066 | 25 | [39 empty] | 2024 | - | Routine Inspection & Maintenance. | bar: A to A; N/A to N/A; Q to A; A to A
79 | TR-103 (WTP SST) | 53105200EE | GSPP2&3 | 0.4 | 22 | 0.4 | 22/0.4 | Auxiliary | 16 | 83 | Healthy | 1016 | 25 | [39 empty] | 2025 | - | Routine Inspection & Maintenance. | bar: A to Q; N/A to N/A; Q to A; A to A
80 | Admin Building SST | 48310781 | GSPP2&3 | 0.5 | 22 | 0.4 | 22/0.4 | Auxiliary | 21 | 91 | Healthy | 730 | 25 | [39 empty] | 2018 | - | Routine Inspection & Maintenance. | bar: A to A; N/A to N/A; Q to A; A to A
81 | 70BFT10 (CTG7A Aux.) | 225309 | GSPP2&3 | 1.5 | 6.6 | 0.4 | 6.6/0.4 | Auxiliary | 3 | 80 | Healthy | 1117 | 25 | A | A | A | A | A | A | A | A | U |  | A | A |  |  |  | A | Q | A | A | A | A | A | A | A | A |  | Q | A | A | A | [9 empty] | 2023 | - | Routine Inspection & Maintenance.
82 | 70BFT20 (CTG7B Aux.) | 225310 | GSPP2&3 | 1.5 | 6.6 | 0.4 | 6.6/0.4 | Auxiliary | 3 | 80 | Healthy | 1152 | 25 | A | A | A | A | A | A | A | A | U |  | A | A |  |  |  | A | Q | A | A | A | A | A | A | A | A |  | Q | A | A | A | [9 empty] | 2023 | - | Routine Inspection & Maintenance.
83 | 71BFT30 (Starting Transformer) | E54623 | GSPP2&3 | 1.25 | 6.6 | 0.69 | 6.6/0.69 | Auxiliary | - | 100 | Healthy | 950 | 25 | [39 empty] | 2025 | - | Routine Inspection & Maintenance. | bar: A to Q; N/A to N/A; Q to A
84 | 72BFT30 (Starting Transformer) | E54624 | GSPP2&3 | 1.25 | 6.6 | 0.69 | 6.6/0.69 | Auxiliary | - | 100 | Healthy | 950 | 25 | [39 empty] | 2025 | - | Routine Inspection & Maintenance. | bar: A to Q; N/A to N/A; Q to A
85 | TR-1 (Coal Handling) | 4104759 | GSPP2&3 | 6 | 22 | 7.2 | 22/7.2 | Auxiliary | 28 | 77 | Monitor | 1117 | 25 | [39 empty] | 2025 | - | Routine Inspection & Maintenance. | bar: A to Q; N/A to N/A; Q to A; A to A
86 | TR-2 (Coal Handling) | 4104758 | GSPP2&3 | 6 | 22 | 7.2 | 22/7.2 | Auxiliary | 28 | 94 | Healthy | 789 | 25 | [39 empty] | 2025 | - | Routine Inspection & Maintenance. | bar: A to Q; N/A to N/A; Q to A; A to A
87 | TR-3 (Coal Handling) | 4104077 | GSPP2&3 | 1.6 | 6.9 | 0.4 | 6.9/0.4 | Auxiliary | 28 | 77 | Monitor | 980 | 25 | [39 empty] | 2025 | - | Routine Inspection & Maintenance. | bar: A to Q; N/A to N/A; Q to A; A to A
88 | TR-4 (Coal Handling) | 4104453 | GSPP2&3 | 1.6 | 6.9 | 0.4 | 6.9/0.4 | Auxiliary | 28 | 71 | Monitor | 678 | 25 | [39 empty] | 2025 | - | Routine Inspection & Maintenance. | bar: A to Q; N/A to N/A; Q to A; A to A
89 | TR-5 (Coal Handling) | xx | GSPP2&3 | 1.6 | 6.9 | 0.4 | 6.9/0.4 | Auxiliary | - | 100 | Healthy | 950 | 25 | [39 empty] | 2025 | - | Routine Inspection & Maintenance. | bar: A to Q; N/A to N/A; Q to A
90 | 1APC-XF-24 (Block1 SUS24) | PCL1429 | GSPP2&3 | 0.862 | 6.9 | 0.4 | 6.9/0.4 | Auxiliary | 27 | 69 | Warning | 1016 | 25 | [39 empty] | 2025 | - | Routine Inspection & Maintenance. | bar: A to Q; N/A to N/A; Q to A; A to A
91 | 2APC-XF-24 (Block2 SUS24) | PCD0277 | GSPP2&3 | 0.862 | 6.9 | 0.4 | 6.9/0.4 | Auxiliary | 18 | 49 | Critical | 1089 | 25 | A | A | A | A | A | A | A |  |  |  | A | A |  |  |  | A | Q | Q | U | A | A | A | A | Q | A |  | Q | A | A | A | [9 empty] | 2025 | - | Routine Inspection & Maintenance.
92 | Coal Harbor Tower 1 | K757927 | GSPP2&3 | 0.8 | 6.9 | 0.4 | 6.9/0.4 | Auxiliary | 25 | 100 | Healthy | 950 | 25 | [39 empty] | 2025 | - | Routine Inspection & Maintenance. | bar: A to Q; N/A to N/A; Q to A; A
93 | Coal Harbor Tower 2 | K757926 | GSPP2&3 | 1 | 6.9 | 0.4 | 6.9/0.4 | Auxiliary | 25 | 100 | Healthy | 950 | 25 | [39 empty] | 2025 | - | Routine Inspection & Maintenance. | bar: A to Q; N/A to N/A; Q to A; A
94 | 1APC-XF-11 (Block1 SUS11) | 332162H5018727A | GSPP2&3 | 2.882 | 6.9 | 0.4 | 6.9/0.4 | Auxiliary | 29 | 90 | Healthy | 950 | 25 | A: A; Q: A; A: A; U: U; A: A; A: A; Q: A; U: Q; A: A; N/A: A; N/A: A; Q: A; A: A; A: A; A: A | [5 empty] | 2017 | - | Routine Inspection & Maintenance.
95 | 1APC-XF-12 (Block1 SUS12) | 332162H501_8727B | GSPP2&3 | 2.882 | 6.9 | 0.4 | 6.9/0.4 | Auxiliary | 29 | 84 | Healthy | 950 | 25 | A: A; Q: A; A: A; U: U; A: A; A: A; Q: Q; U: A; A: A; N/A: A; N/A: A; Q: A; A: A; A: A; A: A | [5 empty] | 2017 | - | Routine Inspection & Maintenance.
96 | 1APC-XF-21 (Block1 SUS21) | 332162H501_8727E | GSPP2&3 | 2.882 | 6.9 | 0.4 | 6.9/0.4 | Auxiliary | 29 | 84 | Healthy | 950 | 25 | [39 empty] | 2017 | - | Routine Inspection & Maintenance. | bar: A to U; N/A to N/A; Q to A
97 | 1APC-XF-22 (Block1 SUS22) | 332162H502_8727F | GSPP2&3 | 2.882 | 6.9 | 0.4 | 6.9/0.4 | Auxiliary | 29 | 84 | Healthy | 950 | 25 | [39 empty] | 2017 | - | Routine Inspection & Maintenance. | bar: A to U; N/A to N/A; Q to A
98 | 1APC-XF-23 (Block1 SUS23) | 331000H509_8727J | GSPP2&3 | 1.333 | 6.9 | 0.4 | 6.9/0.4 | Auxiliary | 29 | 84 | Healthy | 950 | 25 | A: A; Q: A; A: A; U: U; A: A; A: A; Q: Q; N/A: A; N/A: A; Q: A; A: A; A: A; A: A | [5 empty] | 2017 | - | Routine Inspection & Maintenance.
99 | 2APC-XF-11 (Block2 SUS11) | 332152H501_8727C | GSPP2&3 | 2.882 | 6.9 | 0.4 | 6.9/0.4 | Auxiliary | 29 | 84 | Healthy | 950 | 25 | [39 empty] | 2017 | - | Routine Inspection & Maintenance. | bar: A to Q; N/A to N/A; Q to A
100 | 2APC-XF-12 (Block2 SUS12) | 331000H508_8727I | GSPP2&3 | 2.882 | 6.9 | 0.4 | 6.9/0.4 | Auxiliary | 29 | 84 | Healthy | 950 | 25 | A: A; Q: A; A: A; U: A; A: U; A: A; Q: A; U: Q; A: A; N/A: A; N/A: A; Q: A; A: A; A: A; A: A | [5 empty] | 2017 | - | Routine Inspection & Maintenance.
101 | 2APC-XF-21 (Block2 SUS21) | 332162H501_8727D | GSPP2&3 | 2.882 | 6.9 | 0.4 | 6.9/0.4 | Auxiliary | 29 | 84 | Healthy | 950 | 25 | [39 empty] | 2017 | - | Routine Inspection & Maintenance. | bar: A to A; N/A to N/A; Q to A
102 | 2APC-XF-22 (Block2 SUS22) | 332162H502_8727G | GSPP2&3 | 2.882 | 6.9 | 0.4 | 6.9/0.4 | Auxiliary | 29 | 84 | Healthy | 950 | 25 | [39 empty] | 2017 | - | Routine Inspection & Maintenance. | bar: A to Q; N/A to N/A; Q to A
103 | 2APC-XF-23 (Block2 SUS23) | 332162H502_8727H | GSPP2&3 | 1.333 | 6.9 | 0.4 | 6.9/0.4 | Auxiliary | 29 | 84 | Healthy | 950 | 25 | [39 empty] | 2017 | - | Routine Inspection & Maintenance. | bar: A to A; N/A to N/A; Q to A
104 | CFB3 SUS11 | VN85030801_1 | GSPP2&3 | 2.5 | 6.9 | 0.4 | 6.9/0.4 | Auxiliary | 18 | 88 | Healthy | 950 | 25 | [39 empty] | 2018 | - | Routine Inspection & Maintenance. | bar: A to A; N/A to N/A; Q to A
105 | CFB3 SUS12 | VN85030801_2 | GSPP2&3 | 2.5 | 6.9 | 0.4 | 6.9/0.4 | Auxiliary | 18 | 92 | Healthy | 950 | 25 | [39 empty] | 2018 | - | Routine Inspection & Maintenance. | bar: A to A; N/A to N/A; Q to A
106 | Wharehouse SST | FC203816 | GSPP2&3 | 1.6 | 6.9 | 0.4 | 6.9/0.4 | Auxiliary | 17 | 49 | Critical | 1200 | 25 | A | A | A | A | A | A | A | A | A |  | A | A |  |  |  | A | U | Q | U | A | A | A | A | Q | A |  | Q | Q | A | A | [9 empty] | 2019 | - | Routine Inspection & Maintenance.
107 | 51BFT11 (CTG5 SUS11) | 1LKR091730 | GSPP2&3 | 3.325 | 6.9 | 0.4 | 6.9/0.4 | Auxiliary | 17 | 84 | Healthy | 950 | 25 | [39 empty] | 2019 | - | Routine Inspection & Maintenance. | bar: A to A; N/A to N/A; Q to A
108 | 51BFT12 (CTG5 SUS12) | 1LKR091729 | GSPP2&3 | 3.325 | 6.9 | 0.4 | 6.9/0.4 | Auxiliary | 17 | 84 | Healthy | 950 | 25 | [39 empty] | 2019 | - | Routine Inspection & Maintenance. | bar: A to A; N/A to N/A; Q to A
109 | 51BFT13 (Electrochlorination Plant) | 1LKR091731 | GSPP2&3 | 0.4 | 6.9 | 0.4 | 6.9/0.4 | Auxiliary | 17 | 100 | Healthy | 950 | 25 | [39 empty] | 2025 | - | Routine Inspection & Maintenance. | bar: A to Q; N/A to N/A; Q to A
110 | 31BFT10 (CTG3A SUS) | 1LKR050450TER | GSPP2&3 | 1 | 6.9 | 0.4 | 6.9/0.4 | Auxiliary | 21 | 96 | Healthy | 950 | 25 | [39 empty] | 2019 | - | Routine Inspection & Maintenance. | bar: A to U; N/A to N/A; Q to A
111 | 32BFT10 (CTG3B SUS) | 1LKR040038TER | GSPP2&3 | 1 | 6.9 | 0.4 | 6.9/0.4 | Auxiliary | 22 | 93 | Healthy | 950 | 25 | [39 empty] | 2018 | - | Routine Inspection & Maintenance. | bar: A to A; N/A to N/A; Q to A
112 | REC-TR1 (Rectifier) | 6210508 | GSPP2&3 | 0.8 | 6.9 | 0.077 | 6.9/0.077 | Auxiliary | - | 75 | Monitor | 1003 | 25 | [39 empty] | 2025 | - | Routine Inspection & Maintenance. | bar: A to Q; N/A to N/A; Q to A; A to A
113 | REC-TR2 (Rectifier) | 6210509 | GSPP2&3 | 0.8 | 6.9 | 0.077 | 6.9/0.077 | Auxiliary | - | 49 | Critical | 900 | 25 | A | A | A | A | A | A | A |  |  |  | A | A |  |  |  | A | Q | Q | U | A | Q | A | A | A | A |  | A | A | A | A | [9 empty] | 2025 | - | Routine Inspection & Maintenance.
114 | 50MBJ01 (CTG5 SFC) | K810289 | GSPP2&3 | 2.9 | 6.9 | 1.8 | 6.9/1.8 | Auxiliary | 16 | 84 | Healthy | 950 | 25 | [39 empty] | 2019 | - | Routine Inspection & Maintenance. | bar: A to Q; A; N/A to N/A; Q to A
115 | 50MKC01 (CTG5 SEE) | K810290 | GSPP2&3 | 1.43 | 6.9 | 0.5 | 6.9/0.5 | Auxiliary | 16 | 88 | Healthy | 950 | 25 | [39 empty] | 2019 | - | Routine Inspection & Maintenance. | bar: A to Q; A; N/A to N/A; Q to A
116 | 52MKC01 (STG5 SEE) | K810291 | GSPP2&3 | 0.85 | 6.9 | 0.54 | 6.9/0.54 | Auxiliary | 16 | 84 | Healthy | 950 | 25 | [39 empty] | 2019 | - | Routine Inspection & Maintenance. | bar: A to Q; A; N/A to N/A; Q to A
117 | 51PBQ20 | xxx | GSPP2&3 |  |  |  | / | Auxiliary | - | 100 | Healthy | 950 | 25 | [39 empty] | 2025 | - | Routine Inspection & Maintenance. | bar: A to Q; N/A to N/A; Q to A
118 | CFB3 Back Up | 4202021 | GSPP2&3 | 0.5 | 6.9 | 0.4 | 6.9/0.4 | Auxiliary | 27 | 86 | Healthy | 974 | 25 | [39 empty] | 2019 | - | Routine Inspection & Maintenance. | bar: A to A; N/A to N/A; Q to A; A to A
118 | KT51A | 6012333 | MTP-1 | 40 | 115 | 22 | 115/22 | Distribution | 8 | 83 | Healthy | 1089 | 25 | [39 empty] | 2023 | - | Routine Inspection & Maintenance. | bar: A to A; N/A to N/A; Q to A; A to A
118 | EKT51A | 6110289 | MTP-1 | 0.5 | 22 | 0.4 | 22/0.4 | Auxiliary | 8 | 89 | Healthy | 1066 | 25 | [39 empty] | 2023 | - | Routine Inspection & Maintenance. | bar: A to A; N/A to N/A; Q to A; A to A
118 | TR141 | 4011560 | MTP-3 | 1 | 22 | 0.4 | 22/0.4 | Auxiliary | 29 | 97 | Healthy | 1047 | 25 | [39 empty] | 2022 | - | Routine Inspection & Maintenance. | bar: A to A; N/A to N/A; Q to A; A to A
118 | 1BDT10GT001 | 190869 | RDF | 13 | 22 | 6.9 | 22/6.9 | GSUT | 6 | 100 | Healthy | 950 | 25 | [39 empty] | 2025 | - | Routine Inspection & Maintenance. | bar: A to Q; N/A to N/A; Q to A
118 | TR1 | 61310601 | RDF | 3 | 22 | 0.4 | 22/0.4 | Distribution | - | 100 | Healthy | 950 | 25 | [39 empty] | 2025 | - | Routine Inspection & Maintenance. | bar: A to Q; N/A to N/A; Q to A
118 | 1BFT11GT001 | 196057 | RDF | 3 | 6.9 | 0.4 | 6.9/0.4 | Auxiliary | - | 100 | Healthy | 950 | 25 | [39 empty] | 2025 | - | Routine Inspection & Maintenance. | bar: A to Q; N/A to N/A; Q to A
118 | 1BFT12GT001 | 196058 | RDF | 3 | 6.9 | 0.4 | 6.9/0.4 | Auxiliary | - | 100 | Healthy | 950 | 25 | [39 empty] | 2025 | - | Routine Inspection & Maintenance. | bar: A to Q; N/A to N/A; Q to A
118 | SPARE 3 MVA 22/11 kV (Scrap) | 63310466 | Scrap | 3 | 22 | 11 | 22/11 |  | - | 100 | Healthy | 950 | 25 | [39 empty] | 2025 | - | Routine Inspection & Maintenance. | bar: A to Q; N/A to N/A; Q to A
118 | SPARE 0.315 MVA 22/0.4 kV (Scrap) | 3710737 | Scrap | 0.315 | 22 | 0.4 | 22/0.4 |  | 31 | 49 | Critical | 970 | 25 | A | A | A | A | A | A | A | A | A |  | A | A |  |  |  | A | Q | A | U | A | A | A | A | Q | A |  | A | A | A | A | [9 empty] | 2021 | - | Routine Inspection & Maintenance.
118 | SPARE 0.315 MVA 22/0.4 kV (Scrap) | 3710738 | Scrap | 0.315 | 22 | 0.4 | 22/0.4 |  | 31 | 49 | Critical | 1047 | 25 | A | A | A | A | A | A | A | A | A |  | A | A |  |  |  | A | Q | A | U | A | A | A | A | A | A |  | Q | A | A | A | [9 empty] | 2020 | - | Routine Inspection & Maintenance.
118 | SPARE 50 MVA 123/11 kV | 4710346 | SPARE GSPP2&3 | 50 | 123 | 11 | 123/11 |  | 22 | 83 | Healthy | 950 | 25 | A: A; Q: A; A: A; U: A; A: U; A: Q; Q: A; N/A: A; N/A: A; Q: A; A: A; A: A; A: A; A: A | [5 empty] | 2013 | - | Routine Inspection & Maintenance.
118 | SPARE 63.5 MVA 123/11 kV | EDP021401 | SPARE GSPP2&3 | 63.5 | 123 | 11 | 123/11 |  | - | 100 | Healthy | 950 | 25 | [39 empty] | 2025 | - | Routine Inspection & Maintenance. | bar: A to Q; N/A to N/A; Q to A

## System_Guide
GPSC Transformer Asset Management - Enterprise OneDrive Master Dataset
How to use this Excel workbook:
1. Save this file into your team shared OneDrive or Microsoft Teams / SharePoint folder.
2. Sheet "Transformer_Plan" contains the 52-week outage & maintenance tasks.
3. Sheet "Health_Index_Fleet" contains the latest fleet diagnostic evaluation and health indices.
4. You can edit tasks directly here in Excel Online, or edit via the web dashboard.
5. When changes are saved, the web application will automatically sync and update for all team members.